## MV System (Plot-1 & 2)
J7 EMPORIUM
ENGINEERING DIVISION
BOQ FOR TOTAL MV SYSTEM (Emporium Plot-1 & 2)
Sr. No | Item Description | Unit | Req: Qty | Supply Rate | Amount | Remarks
1 | MV Panels (Emporium Plot-1)
1.1 | GDB-MV-P1T1-1 (Rating 11KV Type-Tested) (Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 1250A 3P 50Hz HDHC Tinned Cooper Busbar 25kA for 1 sec including all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 630A 3P VCB Protection Panel= 4No. b) 1250A Bus Coupller Panel= 1No. c) PT Panel on GDB-MV-P1-1 main Bus = 2No. d) Other related Accessories as per SLD. Outgoing Side: a) 630A 3P VCB Protection Panel= 5No. b) CTs 125A/5A= 3No. c) CTs 100A/5A= 12No. d) Including other related Accessories as per SLD. | Nos | 1 |  | 0
1.2 | AIS-P1-1 (Rating 11KV Type-Tested) (Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P 50Hz HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 630A 3P VCB Protection Panel= 1No. b) CTs 300A/5A= 3No. c) PT Panel on Incoming Side = 1No. d) PT Panel on AIS-P1-1 main Bus = 1No. d) Including other related Accessories as per SLD. Outgoing Side: a) 630A 3P VCB Protection Panel= 4No. b) CTs 150A/5A= 6No. c) CTs 100A/5A= 6No. d) Including other related Accessories as per SLD. | Nos | 1 |  | 0
1.3 | AIS-P1-2 (Rating 11KV Type-Tested) (Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 630A 3P VCB Protection Panel= 4No. b) 630A Bus Coupller Panel= 1No. c) CTs 100A/5A= 12No. d) ATS with E&M Interlocking = 2No. e) PT Panel on AIS-P1-2 main Bus = 2No. f) Including other related Accessories as per SLD. Outgoing Side: a) 630A 3P VCB Protection Panel= 2No. b) CTs 100A/5A= 6No. c) Including other related Accessories as per SLD. | Nos | 1 |  | 0
1.4 | AIS-P1-3 (Rating 11KV Type-Tested) (Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 630A 3P VCB Protection Panel= 4No. b) 630A Bus Coupller Panel= 1No. c) CTs 150A/5A= 12No. d) ATS with E&M Interlocking = 2No. e) PT Panel on AIS-P1-2 main Bus = 2No. f) Including other related Accessories as per SLD. Outgoing Side: a) 630A 3P VCB Protection Panel= 2No. b) CTs 150A/5A= 6No. c) Including other related Accessories as per SLD. | Nos | 1 |  | 0
1.5 | AIS-T1 (Rating 11KV Type-Tested) (Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 630A 3P VCB Protection Panel= 2No. b) CTs 125A/5A= 6No. c) ATS with E&M Interlocking = 1No. d) PT Panel on AIS-T1 main Bus = 2No. e) Including other related Accessories as per SLD. Outgoing Side: a) 630A 3P VCB Protection Panel= 2No. b) CTs 125A/5A= 6No. c) Including other related Accessories as per SLD. | Nos | 1 |  | 0
| Total MV Panels (Emporium Plot-1) Exclusive of 17% GST |  |  | 0
| Total MV Panels (Emporium Plot-1) Inclusive of 17% GST |  |  | 0
2 | MV Panels (Emporium Plot-2)
2.1 | GDB-MV-P2T2-1 (Rating 11KV Type-Tested) (Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 1250A 3P HDHC Tinned Cooper Busbar 25kA for 1 sec including all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 630A 3P VCB Protection Panel= 4No. b) 1250A Bus Coupller Panel= 1No. c) PT Panel on GDB-MV-P1-1 main Bus = 2No. d) Other related Accessories as per SLD. Outgoing Side: a) 630A 3P VCB Protection Panel= 5No. b) CTs 125A/5A= 6No. c) CTs 100A/5A= 9No. d) Including other related Accessories as per SLD. | Nos | 1 |  | 0
2.2 | AIS-P2-1 (Rating 11KV Type-Tested) (Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 630A 3P VCB Protection Panel= 1No. b) CTs 300A/5A= 3No. c) PT Panel on Incoming Side = 1No. d) PT Panel on AIS-P1-1 main Bus = 1No. d) Including other related Accessories as per SLD. Outgoing Side: a) 630A 3P VCB Protection Panel= 4No. b) CTs 150A/5A= 6No. c) CTs 100A/5A= 6No. d) Including other related Accessories as per SLD. | Nos | 1 |  | 0
2.3 | AIS-P2-2 (Rating 11KV Type-Tested) (Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 630A 3P VCB Protection Panel= 4No. b) 630A Bus Coupller Panel= 1No. c) CTs 150A/5A= 12No. d) ATS with E&M Interlocking = 2No. e) PT Panel on AIS-P1-2 main Bus = 2No. f) Including other related Accessories as per SLD. Outgoing Side: a) 630A 3P VCB Protection Panel= 2No. b) CTs 150A/5A= 6No. c) Including other related Accessories as per SLD. | Nos | 1 |  | 0
2.4 | AIS-P2-3 (Rating 11KV Type-Tested) (Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 630A 3P VCB Protection Panel= 4No. b) 630A Bus Coupller Panel= 1No. c) CTs 100A/5A= 12No. d) ATS with E&M Interlocking = 2No. e) PT Panel on AIS-P1-2 main Bus = 2No. f) Including other related Accessories as per SLD. Outgoing Side: a) 630A 3P VCB Protection Panel= 2No. b) CTs 100A/5A= 6No. c) Including other related Accessories as per SLD. | Nos | 1 |  | 0
2.5 | AIS-T2 (Rating 11KV Type-Tested) (Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 630A 3P VCB Protection Panel= 2No. b) CTs 125A/5A= 6No. c) ATS with E&M Interlocking = 1No. d) PT Panel on AIS-T1 main Bus = 2No. e) Including other related Accessories as per SLD. Outgoing Side: a) 630A 3P VCB Protection Panel= 2No. b) CTs 125A/5A= 6No. c) Including other related Accessories as per SLD. | Nos | 1 |  | 0
| Total MV Panels (Emporium Plot-2) Exclusive of 17% GST |  |  | 0
| Total MV Panels (Emporium Plot-2) Inclusive of 17% GST |  |  | 0
| G.Total MV Panels (Emporium Plot-1 & 2) Inclusive of 17% GST |  |  | 0

## LV System (Plot-1 & 2)
J7 EMPORIUM
ENGINEERING DIVISION
BOQ FOR TOTAL LV SYSTEM (Emporium Plot-1 & 2)
Sr. No | Item Description | Unit | Req: Qty | Supply Rate | Amount | Remarks
1 | LV Panels (Emporium Plot-1)
1.1 | MDB-P1-1 & MDB-P1-2 (For Podium-1 Chillers rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 3200 AT/AF 4P Adj. ACB Breaker = 1No. b) Digital Power Analyzers comptable with BMS System = 1No. c) Including other related Accessories as per SLD. Outgoing Side: a) 2500 AT/AF 4P Adj. ACB Breaker = 1No. b) 1600 AT/AF 4P Adj. ACB Breaker = 1No. c) 630 AT/AF 4P Adj. MCCB Breaker = 1No. d) 400 AT/AF 4P Adj. MCCB Breaker = 1No. e) 160 AT/AF 4P Adj. MCCB Breaker = 2No. f) with spare space for future = 2No. g) Power Factor Correction Panel (850 kVAR with detuned Reactor = 100kVAR x 7 Steps + 50kVAR x 3 Steps) = 1No. h) Energy (kWH) Meters comptable with BMS System = 5No i) Including other related Accessories as per SLD. | Nos | 2 |  | 0
1.2 | MDB-P1-3 & MDB-P1-4 (For Podium-1 General Loads rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 3200 AT/AF 4P Adj. ACB Breaker = 1No. b) Digital Power Analyzers comptable with BMS System = 1No. c) Including other related Accessories as per SLD. Outgoing Side: a) 1600 AT/AF 4P Adj. ACB Breaker = 2No. b) 1250 AT/AF 4P Adj. ACB Breaker = 1No. c) with spare space for future = 2No. d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No. e) Energy (kWH) Meters comptable with BMS System = 2No f) Including other related Accessories as per SLD. | Nos | 2 |  | 0
1.3 | LSDB-P1-1 (For Podium-1 Life safety DB for Mech-Load rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 800A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 800 AT/AF 4P Adj. MCCB Breaker MA Type = 1No. b) Energy (kWH) Meters comptable with BMS System = 1No. c) 800A ATS = 1No. d) Including other related Accessories as per SLD. Outgoing Side: a) 160A 4P MCCB Breaker MA Type = 1No. b) 63A 4P MCCB Breaker MA Type = 10No c) 40A 4P MCCB Breaker MA Type = 1No d) 32A 4P MCCB Breaker MA Type = 2No c) with spare space for future = 2No. e) Energy (kWH) Meters comptable with BMS System = 14No f) Including other related Accessories as per SLD. | Nos | 1 |  | 0
1.4 | MDB-P1-5 (For Plot-1 Tower-1 rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 3200 AT/AF 4P Adj. ACB Breaker = 1No. b) Digital Power Analyzers comptable with BMS System = 1No. c) Including other related Accessories as per SLD. Outgoing Side: a) 2500 AT/AF 4P Adj. ACB Breaker = 2No. b) 1250 AT/AF 4P Adj. ACB Breaker = 1No. c) with spare space for future = 2No. d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No. e) Energy (kWH) Meters comptable with BMS System = 2No f) Including other related Accessories as per SLD. | Nos | 1 |  | 0
1.5 | MDB-P1-6 (For Plot-1 Tower-2 rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 3200 AT/AF 4P Adj. ACB Breaker = 1No. b) Digital Power Analyzers comptable with BMS System = 1No. c) Including other related Accessories as per SLD. Outgoing Side: a) 2500 AT/AF 4P Adj. ACB Breaker = 2No. b) 1250 AT/AF 4P Adj. ACB Breaker = 1No. c) 1000 AT/AF 4P Adj. MCCB Breaker = 1No d) 400 AT/AF 4P Adj. MCCB Breaker = 1No c) with spare space for future = 2No. d) Power Factor Correction Panel (750 kVAR with detuned Reactor = 75kVAR x 9 Steps + 25kVAR x 3 Steps) = 1No. e) Energy (kWH) Meters comptable with BMS System = 4No f) Including other related Accessories as per SLD. | Nos | 1 |  | 0
1.6 | LSDB-P1-2 (For Podium-1 Life safety DB for Mech-Load rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 400A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 400 AT/AF 4P Adj. MCCB Breaker MA Type = 1No. b) Energy (kWH) Meters comptable with BMS System = 1No. c) 400A ATS = 1No. d) Including other related Accessories as per SLD. Outgoing Side: a) 160A 4P MCCB Breaker MA Type = 2No. b) 40A 4P MCCB Breaker MA Type = 1No c) with spare space for future = 2No. d) Energy (kWH) Meters comptable with BMS System = 3No e) Including other related Accessories as per SLD. | Nos | 1 |  | 0
| Total LV Panels (Emporium Plot-1) Exclusive of 17% GST |  |  | 0
| Total LV Panels (Emporium Plot-1) Inclusive of 17% GST |  |  | 0
2 | LV Panels (Emporium Plot-2)
2.1 | MDB-P2-1 (For Podium-2 Chillers rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 3200 AT/AF 4P Adj. ACB Breaker = 1No. b) Digital Power Analyzers comptable with BMS System = 1No. c) Including other related Accessories as per SLD. Outgoing Side: a) 2500 AT/AF 4P Adj. ACB Breaker = 1No. b) 1600 AT/AF 4P Adj. ACB Breaker = 1No. c) 250 AT/AF 4P Adj. MCCB Breaker = 2No. d) 160 AT/AF 4P Adj. MCCB Breaker = 2No. e) with spare space for future = 2No. f) Power Factor Correction Panel (850 kVAR with detuned Reactor = 100kVAR x 7 Steps + 50kVAR x 3 Steps) = 1No. g) Energy (kWH) Meters comptable with BMS System = 5No h) Including other related Accessories as per SLD. | Nos | 1 |  | 0
2.2 | MDB-P2-2 (For Podium-2 Chillers rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 3200 AT/AF 4P Adj. ACB Breaker = 1No. b) Digital Power Analyzers comptable with BMS System = 1No. c) Including other related Accessories as per SLD. Outgoing Side: a) 1600 AT/AF 4P Adj. ACB Breaker = 2No. b) 630 AT/AF 4P Adj. MCCB Breaker = 1No c) 400 AT/AF 4P Adj. MCCB Breaker = 1No. d) 160 AT/AF 4P Adj. MCCB Breaker = 2No. e) with spare space for future = 2No. f) Power Factor Correction Panel (850 kVAR with detuned Reactor = 100kVAR x 7 Steps + 50kVAR x 3 Steps) = 1No. g) Energy (kWH) Meters comptable with BMS System = 5No h) Including other related Accessories as per SLD. | Nos | 1 |  | 0
2.3 | MDB-P2-3 & MDB-P2-4 (For Podium-2 General Loads rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 3200 AT/AF 4P Adj. ACB Breaker = 1No. b) Digital Power Analyzers comptable with BMS System = 1No. c) Including other related Accessories as per SLD. Outgoing Side: a) 1600 AT/AF 4P Adj. ACB Breaker = 2No. b) 1250 AT/AF 4P Adj. ACB Breaker = 1No. c) with spare space for future = 2No. d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No. e) Energy (kWH) Meters comptable with BMS System = 2No f) Including other related Accessories as per SLD. | Nos | 2 |  | 0
2.4 | LSDB-P2-1 (For Podium-2 Life safety DB for Mech-Load rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 800A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 800 AT/AF 4P Adj. MCCB Breaker MA Type = 1No. b) Energy (kWH) Meters comptable with BMS System = 1No. c) 800A ATS = 1No. d) Including other related Accessories as per SLD. Outgoing Side: a) 160A 4P MCCB Breaker MA Type = 1No. b) 63A 4P MCCB Breaker MA Type = 10No c) 40A 4P MCCB Breaker MA Type = 1No d) 32A 4P MCCB Breaker MA Type = 1No c) with spare space for future = 2No. e) Energy (kWH) Meters comptable with BMS System = 13No f) Including other related Accessories as per SLD. | Nos | 1 |  | 0
2.5 | MDB-P2-5 (For Plot-2 Tower-1 rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 3200 AT/AF 4P Adj. ACB Breaker = 1No. b) Digital Power Analyzers comptable with BMS System = 1No. c) Including other related Accessories as per SLD. Outgoing Side: a) 2500 AT/AF 4P Adj. ACB Breaker = 2No. b) 1250 AT/AF 4P Adj. ACB Breaker = 1No. c) with spare space for future = 2No. d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No. e) Energy (kWH) Meters comptable with BMS System = 2No f) Including other related Accessories as per SLD. | Nos | 1 |  | 0
2.6 | MDB-P2-6 (For Plot-2 Tower-2 rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 3200 AT/AF 4P Adj. ACB Breaker = 1No. b) Digital Power Analyzers comptable with BMS System = 1No. c) Including other related Accessories as per SLD. Outgoing Side: a) 2500 AT/AF 4P Adj. ACB Breaker = 2No. b) 1250 AT/AF 4P Adj. ACB Breaker = 1No. c) 1000 AT/AF 4P Adj. MCCB Breaker = 1No d) 400 AT/AF 4P Adj. MCCB Breaker = 1No c) with spare space for future = 2No. d) Power Factor Correction Panel (750 kVAR with detuned Reactor = 75kVAR x 9 Steps + 25kVAR x 3 Steps) = 1No. e) Energy (kWH) Meters comptable with BMS System = 4No f) Including other related Accessories as per SLD. | Nos | 1 |  | 0
2.7 | LSDB-P2-2 (For Podium Life safety DB for Mech-Load rating 400V) (Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 400A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD) Incoming Side: a) 400 AT/AF 4P Adj. MCCB Breaker MA Type = 1No. b) Energy (kWH) Meters comptable with BMS System = 1No. c) 400A ATS = 1No. d) Including other related Accessories as per SLD. Outgoing Side: a) 160A 4P MCCB Breaker MA Type = 2No. b) 40A 4P MCCB Breaker MA Type = 1No c) with spare space for future = 2No. d) Energy (kWH) Meters comptable with BMS System = 3No e) Including other related Accessories as per SLD. | Nos | 1 |  | 0
| Total LV Panels (Emporium Plot-2) Exclusive of 17% GST |  |  | 0
| Total LV Panels (Emporium Plot-2) Inclusive of 17% GST |  |  | 0
| G.Total LV Panels (Emporium Plot-1 & 2) Inclusive of 17% GST |  |  | 0

## Bus Ducted System (Plot-1 & 2)
J7 EMPORIUM
ENGINEERING DIVISION
BOQ FOR Bus Ducted SYSTEM (Emporium Plot-1 & 2)
Sr. No | Item Description | Unit | Req: Qty | Supply Rate | Amount | Remarks
A | Bus Ducted System
Bus Ducted System (Horizontal/Vertical) shall be (Type Tested) complied with IEC-61439-6 (65kA Short-circuiting Rating for 1 Sec) of Aluminium type fully Insulated Compacted & of Rigid construction having rigidly constructed enclosure from electro-galvanized sheet steel of 2mm thickness, IP66 Rating having 5No Aluminium Busbars included with phase indication comprising of (3Ph/N/50% Earth rated at 400V 50Hz), comprising with all external galvanized steel supports & brackets suitable for fixing on walls/ceiling and related materials e.g. elbows, joints, flang ends, flang end boxes, Tap-off Units, end caps, end enclosures, expansion units, vertical spring hangers, horizontal & Vertical Hangers, or any related material required to complete the job in all respect.
1 | Bus Trunking Duct (Emporium Plot-1) (Podium-1)
1.1 | BTD (Vertical) from MDB-P1-3 & MDB-P1-4 (Podium-1/Plot-1) | R.Mtr | 171.56 |  | 0
1600A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = 42.89Mtr x 4No
1.2 | BTD (Vertical) from MDB-P1-3 & MDB-P1-4 (Podium-1/Plot-1) | R.Mtr | 19.2 |  | 0
800A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = 4.80Mtr x 4No
1.3 | Tap-Off Box with removable bottom cover & Rotary handle type with Mechanical Interlocking equiped with internal barriers to prevent accidental contact with live parts at the terminals of the protective device & "Danger" Warning Sign of an approved type shall be provided on the front panel of Tap-Off Box. |  |  |  | 0
a | 630A Tap-Off Box | Nos | 5
b | 400A Tap-Off Box | Nos | 9
c | 250A Tap-Off Box | Nos | 1
d | 160A Tap-Off Box | Nos | 2
e | 100A Tap-Off Box | Nos | 2
f | 63A Tap-Off Box | Nos | 2
g | 32A Tap-Off Box | Nos | 1
h | Provision for Tap-Off Box | Nos | 22
| Total Bus Riser System (Emporium Plot-1) Podium-1 Exclusive of 17% GST |  |  | 0
| Total Bus Riser System (Emporium Plot-1) Podium-1 Inclusive of 17% GST |  |  | 0
2 | Bus Trunking Duct (Emporium Plot-1) (Tower-1 & 2)
2.1 | BTD (Vertical) from MDB-P1-5 & MDB-P1-6 (Tower-1 & 2/Plot-1) | R.Mtr | 241.52 |  | 0
2500A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = (56.76Mtr x 2No) + (64Mtr x 2No)
2.2 | BTD (Vertical) from MDB-P1-5 & MDB-P1-6 (Tower-1 & 2/Plot-1) | R.Mtr | 46.01 |  | 0
1000A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = (7.16Mtr x 2No) + (31.69 x 1No)
2.3 | BTD (Vertical) from MDB-P1-6 (Tower-2/Plot-1) | R.Mtr | 21.48 |  | 0
800A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = 10.74Mtr x 2No
2.4 | BTD (Vertical) from MDB-P1-6 (Tower-2/Plot-1) | R.Mtr | 78.25 |  | 0
400A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = 78.25Mtr x 1No
2.5 | Tap-Off Box with removable bottom cover & Rotary handle type with Mechanical Interlocking equiped with internal barriers to prevent accidental contact with live parts at the terminals of the protective device & "Danger" Warning Sign of an approved type shall be provided on the front panel of Tap-Off Box. |  |  |  | 0
a | 160A Tap-Off Box | Nos | 37
b | Provision for Tap-Off Box | Nos | 37
| Total Bus Riser System (Emporium Plot-1) Tower-1 & 2 Exclusive of 17% GST |  |  | 0
| Total Bus Riser System (Emporium Plot-1) Tower-1 & 2 Inclusive of 17% GST |  |  | 0
| G.Total Bus Riser System (Emporium Plot-1) Inclusive of 17% GST |  |  | 0
3 | Bus Trunking Duct (Emporium Plot-2) (Podium-2)
3.1 | BTD (Vertical) from MDB-P2-3 & MDB-P2-4 (Podium-2/Plot-2) | R.Mtr | 171.56 |  | 0
1600A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = 42.89Mtr x 4No
3.2 | BTD (Vertical) from MDB-P2-3 & MDB-P2-4 (Podium-2/Plot-2) | R.Mtr | 19.2 |  | 0
800A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = 4.80Mtr x 4No
3.3 | Tap-Off Box with removable bottom cover & Rotary handle type with Mechanical Interlocking equiped with internal barriers to prevent accidental contact with live parts at the terminals of the protective device & "Danger" Warning Sign of an approved type shall be provided on the front panel of Tap-Off Box. |  |  |  | 0
a | 630A Tap-Off Box | Nos | 5
b | 400A Tap-Off Box | Nos | 9
c | 250A Tap-Off Box | Nos | 1
d | 160A Tap-Off Box | Nos | 2
e | 100A Tap-Off Box | Nos | 2
f | 63A Tap-Off Box | Nos | 2
g | 32A Tap-Off Box | Nos | 1
h | Provision for Tap-Off Box | Nos | 22
| Total Bus Riser System (Emporium Plot-2) Podium-2 Exclusive of 17% GST |  |  | 0
| Total Bus Riser System (Emporium Plot-2) Podium-2 Inclusive of 17% GST |  |  | 0
4 | Bus Trunking Duct (Emporium Plot-2) (Tower-1 & 2)
4.1 | BTD (Vertical) from MDB-P2-5 & MDB-P2-6 (Tower-1 & 2/Plot-2) | R.Mtr | 241.36 |  | 0
2500A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = (60.34Mtr x 4No)
4.2 | BTD (Vertical) from MDB-P2-5 & MDB-P2-6 (Tower-1 & 2/Plot-2) | R.Mtr | 47.77 |  | 0
1000A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = (47.77Mtr x 1No)
4.3 | BTD (Vertical) from MDB-P2-6 (Tower-2/Plot-2) | R.Mtr | 76.48 |  | 0
800A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = 19.12Mtr x 4No
4.4 | BTD (Vertical) from MDB-P2-6 (Tower-2/Plot-2) | R.Mtr | 81.83 |  | 0
400A Aluminium BTD (Type Tested) IP66, 65kA for 1 Sec, (3Ph/N/50% Earth) = 81.83Mtr x 1No
4.5 | Tap-Off Box with removable bottom cover & Rotary handle type with Mechanical Interlocking equiped with internal barriers to prevent accidental contact with live parts at the terminals of the protective device & "Danger" Warning Sign of an approved type shall be provided on the front panel of Tap-Off Box. |  |  |  | 0
a | 250A Tap-Off Box | Nos | 27
b | 160A Tap-Off Box | Nos | 14
c | Provision for Tap-Off Box | Nos | 41
| Total Bus Riser System (Emporium Plot-2) Tower-1 & 2 Exclusive of 17% GST |  |  | 0
| Total Bus Riser System (Emporium Plot-2) Tower-1 & 2 Inclusive of 17% GST |  |  | 0
| G.Total Bus Riser System (Emporium Plot-2) Inclusive of 17% GST |  |  | 0
| G.Total Bus Riser System (Emporium Plot-1 & 2) Inclusive of 17% GST |  |  | 0
5 | Bus Trunking Duct Hanging Support System and related Materials to complete the Installation Job in all respect (Unit Price)
5.1 | Horizontal Length (BTD) | No | 1
5.2 | Flexiable Links Braided Type | No | 1
5.3 | Flang End | No | 1
5.4 | Flang End Boxes | No | 1
5.5 | End Caps | No | 1
5.6 | End Enclosures | No | 1
5.7 | Wall Flange | No | 1
5.8 | Flatwise Elbow | No | 1
5.9 | Cable Tap Box | No | 1
5.1 | Edgewise Elbow | No | 1
5.11 | Tee Elbow | No | 1
5.12 | Elbow (Normal) | No | 1
5.13 | Edgewise Offset | No | 1
5.14 | Joint (Standard Normal) | No | 1
5.15 | Joint (with Predective Temperature Rise Indicator) | No | 1
5.16 | Spring Hanger Vertical | No | 1
5.17 | Hanger Vertical | No | 1
5.18 | Hanger Horizontal | No | 1 |  | 0