## MV System (Plot-1 & 2)
J7 EMPORIUM
ENGINEERING DIVISION
MV SYSTEM (Emporium Plot-1 & 2)
Description |  |  |  | Vendor:
Enclosure:
Brand:
Product:
Sr. No | Item Description | Unit | Req: Qty | Supply Rate | Amount | Remarks
1 | (Emporium Plot-1) (Podium-1, Tower-1&2)
1.1 | GDB-MV-P1T1-1 (Rating 11KV Type-Tested) (Plot-1 Podium-1/ Tower-1 & 2:) | Nos | 1 |  | 0
(Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 1250A 3P 50Hz HDHC Tinned Cooper Busbar 25kA for 1 sec including all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 630A 3P VCB Protection Panel= 4No.
b) 1250A Bus Coupller Panel= 1No.
c) PT Panel on GDB-MV-P1T1-1 main Bus = 2No.
d) Other related Accessories as per SLD.
Outgoing Side:
a) 630A 3P VCB Protection Panel= 5No.
b) CTs 125A/5A= 3No.
c) CTs 100A/5A= 12No.
d) Including other related Accessories as per SLD.
1.2 | AIS-P1-1 (Rating 11KV Type-Tested): (Plot-1 Podium-1) | Nos | 1 |  | 0
(Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P 50Hz HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD) )
Incoming Side:
a) 630A 3P VCB Protection Panel= 1No.
b) CTs 300A/5A= 3No.
c) PT Panel on Incoming Side = 1No.
d) PT Panel on AIS-P1-1 main Bus = 1No.
e) Including other related Accessories as per SLD.
Outgoing Side:
a) 630A 3P VCB Protection Panel= 4No.
b) CTs 150A/5A= 6No.
c) CTs 100A/5A= 6No.
d) Including other related Accessories as per SLD.
1.3 | AIS-P1-2 (Rating 11KV Type-Tested): (Plot-1 Podium-1) | Nos | 1 |  | 0
(Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 630A 3P VCB Protection Panel= 4No.
b) 630A Bus Coupller Panel= 1No.
c) CTs 100A/5A= 12No.
d) ATS with E&M Interlocking = 2No.
e) PT Panel on AIS-P1-2 main Bus = 2No.
f) Including other related Accessories as per SLD.
Outgoing Side:
a) 630A 3P VCB Protection Panel= 2No.
b) CTs 100A/5A= 6No
c) Including other related Accessories as per SLD.
1.4 | AIS-P1-3 (Rating 11KV Type-Tested): (Plot-1 Podium-1) | Nos | 1 |  | 0
(Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 630A 3P VCB Protection Panel= 4No.
b) 630A Bus Coupller Panel= 1No.
c) CTs 150A/5A= 12No.
d) ATS with E&M Interlocking = 2No.
e) PT Panel on AIS-P1-3 main Bus = 2No.
f) Including other related Accessories as per SLD.
Outgoing Side:
a) 630A 3P VCB Protection Panel= 2No.
b) CTs 100A/5A= 6No
c) Including other related Accessories as per SLD.
1.5 | AIS-T1 (Rating 11KV Type-Tested): (Plot-1 Tower-1 & 2) | Nos | 1 |  | 0
(Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 630A 3P VCB Protection Panel= 2No.
b) CTs 125A/5A= 6No.
c) ATS with E&M Interlocking = 1No.
d) PT Panel on AIS-T1 main Bus = 2No.
e) Including other related Accessories as per SLD.
Outgoing Side:
a) 630A 3P VCB Protection Panel= 2No.
b) CTs 125A/5A= 6No.
c) Including other related Accessories as per SLD.
2 | (Emporium Plot-2) (Podium-2 Tower-1 & 2)
2.1 | GDB-MV-P2T2-1 (Rating 11KV Type-Tested) (Plot-2 Podium-2/ Tower-1 & 2:) | Nos | 1 |  | 0
(Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 1250A 3P HDHC Tinned Cooper Busbar 25kA for 1 sec including all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 630A 3P VCB Protection Panel= 4No.
b) 1250A Bus Coupller Panel= 1No.
c) PT Panel on GDB-MV-P2T2-1 main Bus = 2No.
d) Other related Accessories as per SLD.
Outgoing Side:
a) 630A 3P VCB Protection Panel= 5No.
b) CTs 125A/5A= 6No.
c) CTs 100A/5A= 9No.
d) Including other related Accessories as per SLD.
2.2 | AIS-P2-1 (Rating 11KV Type-Tested): (Podium-2) | Nos | 1 |  | 0
(Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 630A 3P VCB Protection Panel= 1No.
b) CTs 300A/5A= 3No.
c) PT Panel on Incoming Side = 1No.
d) PT Panel on AIS-P2-1 main Bus = 1No.
e) Including other related Accessories as per SLD.
Outgoing Side:
a) 630A 3P VCB Protection Panel= 4No.
b) CTs 150A/5A= 6No.
c) CTs 100A/5A= 6No.
d) Including other related Accessories as per SLD.
2.3 | AIS-P2-2 (Rating 11KV Type-Tested): (Podium-2) | Nos | 1 |  | 0
(Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 630A 3P VCB Protection Panel= 4No.
b) 630A Bus Coupller Panel= 1No.
c) CTs 150A/5A= 12No.
d) ATS with E&M Interlocking = 2No.
e) PT Panel on AIS-P2-2 main Bus = 2No.
f) Including other related Accessories as per SLD.
Outgoing Side:
a) 630A 3P VCB Protection Panel= 2No.
b) CTs 150A/5A= 6No
c) Including other related Accessories as per SLD.
2.4 | AIS-P2-3 (Rating 11KV Type-Tested): (Podium-2) | Nos | 1 |  | 0
(Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 630A 3P VCB Protection Panel= 4No.
b) 630A Bus Coupller Panel= 1No.
c) CTs 100A/5A= 12No.
d) ATS with E&M Interlocking = 2No.
e) PT Panel on AIS-P2-3 main Bus = 2No.
f) Including other related Accessories as per SLD.
Outgoing Side:
a) 630A 3P VCB Protection Panel= 2No.
b) CTs 100A/5A= 6No
c) Including other related Accessories as per SLD.
2.5 | AIS-T2 (Rating 11KV Type-Tested): (Tower-1 & 2) | Nos | 1 |  | 0
(Metal Clad Sheet Fabricated, totally enclosed, 12SWG thickness indoor type Panel, 630A 3P HDHC Tinned Cooper Busbar 25kA for 3 sec including all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 630A 3P VCB Protection Panel= 2No.
b) CTs 125A/5A= 6No.
c) ATS with E&M Interlocking = 1No.
d) PT Panel on AIS-T1 main Bus = 2No.
e) Including other related Accessories as per SLD.
Outgoing Side:
a) 630A 3P VCB Protection Panel= 2No.
b) CTs 125A/5A= 6No.
c) Including other related Accessories as per SLD.
| Trolley for All switchboards |  | 10
Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Exclusive GST/SST |  |  |  | 0
GST/SST |  |  |  | 0
G.Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Inclusive of GST/SST |  |  |  | 0