## BOQ for Floor DB's & Isolator (hidden)
BOQ for Power Distribution System (Floor DB's & Isolators)
for Basements, Ground-1 & 2, 1st, 2nd & 2A Floor for J7 Emporium Plot No: 1
S.No | Description | Unit | Qty | Supply Rate (PKR) | Supply Amount (PKR) | Remarks
A | LV Distribution Boards
1 | Floor Distribution Boards (FDBs)
Floor DBs shall be complied with BS EN 61349 with rating of 400V/230V 50Hz/ Water & Dust Proof IP42 Rating / Form 2b/ Wall Mounted (Non-Type Tested) Panels/ fabricated from 14 s.w.g sheet steel complete with hinged covers, the free end of which shall be secured by captive knurled thumb screws and chrome-plated lockable handle, gaskets, solid type concealed hinges, detachable undrilled end plates fitted top and bottom and external wall fixing lugs arranged to provide a small air gap between the back of the board and the wall. Including all related items e.g. MCBs/MCCB/Volt Meters/Ameters/ Selectors switches/Phase Indication Lamps/ Shunt trip Unit/Earth Leakage Relay with Toroid CT/ CTs/ Energy Kwh Meters with BMS/EMS Compatability and any other related equipments required to complete the job in all respect as per Single Line Diagram (SLD) & specifictions.
1.1 | FDB-P1-B3-1 | Nos. | 1 |  | 0
Input Side:
a) 160A 4P MCCB 18KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Digital Voltmeter with Selector Switch = 1No
d) Digital Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 150A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 100A 4P MCB 10KA = 1No
b) 40A 4P MCB 10KA = 1No
c) 32A 4P MCB 10KA = 3No
d) Spare Space = 2No
1.2 | FDB-P1-B3-2 | Nos. | 1 |  | 0
Input Side:
a) 63A 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Digital Voltmeter with Selector Switch = 1No
d) Digital Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 100A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 40A 4P MCB 10KA = 1No
c) 32A 4P MCB 10KA = 2No
d) Spare Space = 2No
1.3 | Isolators for B3 Floor:
| a) 100A Isolator | Nos. | 1
1.4 | FDB-P1-B2-1 | Nos. | 1 |  | 0
Input Side:
a) 100A 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Digital Voltmeter with Selector Switch = 1No
d) Digital Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 100A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 40A 4P MCB 10KA = 2No
b) 32A 4P MCB 10KA = 2No
c) 32A 2P MCB 10KA = 2No
d) Spare Space = 2No
1.5 | FDB-P1-B2-2 | Nos. | 1 |  | 0
Input Side:
a) 32A 4P MCCB 10KA = 1No
b) 2A 6KA Control Circuit Breaker = 3No
c) Digital Voltmeter with Selector Switch = 1No
d) Digital Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 50A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 32A 4P MCB 10KA = 2No
b) 32A 2P MCB 10KA = 2No
c) Spare Space = 2No
1.6 | Isolators for B2 Floor:
| a) 40A Isolator | Nos. | 2
1.7 | FDB-P1-B1-1 | Nos. | 1 |  | 0
Input Side:
a) 100A 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Digital Voltmeter with Selector Switch = 1No
d) Digital Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 100A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 40A 4P MCB 10KA = 2No
b) 32A 4P MCB 10KA = 4No
c) Spare Space = 2No
1.8 | FDB-P1-B1-2 | Nos. | 1 |  | 0
Input Side:
a) 100A 4P MCCB 10KA = 1No
b) 2A 6KA Control Circuit Breaker = 3No
c) Digital Voltmeter with Selector Switch = 1No
d) Digital Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 100A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 32A 4P MCB 10KA = 4No
c) Spare Space = 2No
1.9 | Isolators for B1 Floor:
| a) 40A Isolator | Nos. | 2
1.1 | FDB-P1-G1-1 | Nos. | 1 |  | 0
Input Side:
a) 630AF/630AT 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 600A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 40A 4P MCB 10KA = 1No
c) 32A 4P MCB 10KA = 16No
d) Spare Space = 2No
e) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 14No
1.11 | FDB-P1-G1-2 | Nos. | 1 |  | 0
Input Side:
a) 630AF/630AT 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 600A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 32A 4P MCB 10KA = 15No
c) Spare Space = 2No
d) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 14No
1.12 | Isolators for G1 Floor:
| a) 40A Isolator | Nos. | 1
| b) 32A Isolator | Nos. | 27
1.13 | FDB-P1-G2-1 | Nos. | 1 |  | 0
Input Side:
a) 400AF/400AT 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 400A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 150A 4P MCB 18KA = 1No
b) 63A 4P MCB 10KA = 1No
c) 32A 4P MCB 10KA = 13No
d) Spare Space = 2No
e) Space for Digital dual source Kwh Meter (DYN Rail Assembly) with BMS/EMS compatible - Protocal BACnet RS-485 network. = 14No
f) Space for CT's for each Digital dual source Kwh Meter = 42No
1.14 | FDB-P1-G2-2 | Nos. | 1 |  | 0
Input Side:
a) 630AF/630AT 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 600A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 40A 4P MCB 10KA = 2No
c) 32A 4P MCB 10KA = 16No
d) Spare Space = 3No
e) Space for Digital dual source Kwh Meter (DYN Rail Assembly) with BMS/EMS compatible - Protocal BACnet RS-485 network. = 14No
f) Space for CT's for each Digital dual source Kwh Meter = 42No
1.15 | Isolators for G2 Floor:
| a) 150A Isolator | Nos. | 1
| b) 40A Isolator | Nos. | 2
| c) 32A Isolator | Nos. | 25
1.16 | FDB-P1-1F-1 | Nos. | 1 |  | 0
Input Side:
a) 400AF/400AT 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 400A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 32A 4P MCB 10KA = 14No
c) Spare Space = 2No
d) Space for Digital dual source Kwh Meter (DYN Rail Assembly) with BMS/EMS compatible - Protocal BACnet RS-485 network. = 13No
e) Space for CT's for each Digital dual source Kwh Meter = 39No
1.17 | FDB-P1-1F-2 | Nos. | 1 |  | 0
Input Side:
a) 400AF/400AT 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 400A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 32A 4P MCB 10KA = 13No
c) Spare Space = 2No
d) Space for Digital dual source Kwh Meter (DYN Rail Assembly) with BMS/EMS compatible - Protocal BACnet RS-485 network. = 10No
e) Space for CT's for each Digital dual source Kwh Meter = 30No
1.18 | Isolators for 1F Floor:
| a) 32A Isolator | Nos. | 25
1.19 | FDB-P1-2F-1 | Nos. | 1 |  | 0
Input Side:
a) 250AF/250AT 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 250A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 40A 4P MCB 10KA = 1No
b) 32A 4P MCB 10KA = 12No
c) Spare Space = 2No
d) Space for Digital dual source Kwh Meter (DYN Rail Assembly) with BMS/EMS compatible - Protocal BACnet RS-485 network. = 10No
e) Space for CT's for each Digital dual source Kwh Meter = 30No
1.2 | FDB-P1-2F-2 | Nos. | 1 |  | 0
Input Side:
a) 250AF/250AT 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 250A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 40A 4P MCB 10KA = 2No
c) 32A 4P MCB 10KA = 10No
d) Spare Space = 2No
e) Space for Digital dual source Kwh Meter (DYN Rail Assembly) with BMS/EMS compatible - Protocal BACnet RS-485 network. = 8No
f) Space for CT's for each Digital dual source Kwh Meter = 24No
1.21 | Isolators for 2F Floor:
| a) 63A Isolator | Nos. | 1
| b) 40A Isolator | Nos. | 2
| c) 32A Isolator | Nos. | 17
1.22 | FDB-P1-2AF-1 | Nos. | 1 |  | 0
Input Side:
a) 250AF/250AT 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 250A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 32A 4P MCB 10KA = 13No
b) Spare Space = 2No
c) Space for Digital dual source Kwh Meter (DYN Rail Assembly) with BMS/EMS compatible - Protocal BACnet RS-485 network. = 10No
d) Space for CT's for each Digital dual source Kwh Meter = 30No
1.23 | FDB-P1-2AF-2 | Nos. | 1 |  | 0
Input Side:
a) 250AF/250AT 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 250A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 160A 4P MCB 18KA = 1No
b) 63A 4P MCB 10KA = 1No
c) 40A 4P MCB 10KA = 2No
d) 32A 4P MCB 10KA = 7No
e) Spare Space = 2No
f) Space for Digital dual source Kwh Meter (DYN Rail Assembly) with BMS/EMS compatible - Protocal BACnet RS-485 network. = 7No
g) Space for CT's for each Digital dual source Kwh Meter = 21No
1.24 | Isolators for 2AF Floor:
| a) 160A Isolator | Nos. | 1
| b) 63A Isolator | Nos. | 1
| c) 40A Isolator | Nos. | 2
| d) 32A Isolator | Nos. | 15
TOTAL |  | PKR |  |  | 0
Note:
1) All the Distribution Boards (Floor Distribution Boards (FDB) & MSSB DB's) must have Voltmeter,Ammeter, Selector Switch, Phase Indication Lamps.
2) All the Distribution Boards (Comman Area (CA) DB's, Mechanical (ME) DB's, Fire Command Center (FCC) DB's)
must have Voltmeter, Selector Switch, Phase Indication Lamps.
3) Kindly Quote your final and Discounted rates for supply, Installation & Final Testing/Commissioning in all respect according to the BOQ items.
4) Do your value engineering as well and provide options if applicable and highlight those items as well, we will be obliged for your feedback.
5) If the items which you cannot provide please mention them as well in the BOQ.
6) Please study the schematic drawings as well as Specifications so that the items to be quoted must follow the specifications
7) Provide Technical specifications for all of the items mentioned in the BOQ or which you will add, and clearly highlight those item models

## BOQ for Common Area DB's (hidden)
BOQ for Power Distribution System (Common Area DB's)
for Basements, Ground-1 & 2, 1st, 2nd & 2A Floor for J7 Emporium Plot No: 1
S.No | Description | Unit | Qty | Supply Rate (PKR) | Supply Amount (PKR) | Remarks
A | LV Distribution Boards
2 | Common Area Distribution Boards (CA)
Comman Area DBs shall be complied with BS EN 61349 with rating of 400V/230V 50Hz/ Water & Dust Proof of (IP42 Rating/Form 1/Wall Mounted (Non-Type Tested) Panels/ fabricated from 14 s.w.g sheet steel complete with hinged covers, the free end of which shall be secured by captive knurled thumb screws and chrome-plated lockable handle, gaskets, solid type concealed hinges, detachable undrilled end plates fitted top and bottom and external wall fixing lugs arranged to provide a small air gap between the back of the board and the wall. Including all related items e.g. MCBs/MCCBs/Phase Indication Lamps/Shunt trip Unit/Earth Leakage Relay with Toroid CT/Relay Modules with BMS/EMS Compatability and any other related equipments required to complete the job in all respect as per Single Line Diagram (SLD) & specifictions.
2.1 | DB-P1-B3-CA1 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 15No
b) 20A SP MCB 10KA = 7No
c) Spare Space = 5No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 11No
2.2 | DB-P1-B3-CA2 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 19No
b) 20A SP MCB 10KA = 2No
c) Spare Space = 6No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 19No
2.3 | DB-P1-B3-CA3 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 12No
b) 20A SP MCB 10KA = 3No
c) Spare Space = 3No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 10No
2.4 | DB-P1-B3-CA4 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 21No
b) 20A SP MCB 10KA = 3No
c) Spare Space = 6No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 20No
2.5 | DB-P1-B2-CA1 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 14No
b) 20A SP MCB 10KA = 6No
c) Spare Space = 7No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 10No
2.6 | DB-P1-B2-CA2 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 22No
b) 20A SP MCB 10KA = 3No
c) Spare Space = 5No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 22No
2.7 | DB-P1-B2-CA3 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 11No
b) 20A SP MCB 10KA = 3No
c) Spare Space = 4No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 9No
2.8 | DB-P1-B2-CA4 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 20No
b) 20A SP MCB 10KA = 3No
c) Spare Space = 7No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 19No
2.9 | DB-P1-B1-CA1 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 13No
b) 20A SP MCB 10KA = 6No
c) Spare Space = 5No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 9No
2.1 | DB-P1-B1-CA2 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 22No
b) 20A SP MCB 10KA = 3No
c) Spare Space = 5No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 22No
2.11 | DB-P1-B1-CA4 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 26No
b) 20A SP MCB 10KA = 8No
c) Spare Space = 8No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 22No
2.12 | DB-P1-G1-CA1 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 27No
b) 20A SP MCB 10KA = 4No
c) Spare Space = 8No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 25No
2.13 | DB-P1-G1-CA2 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 17No
b) 20A SP MCB 10KA = 2No
c) Spare Space = 5No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 16No
2.14 | DB-P1-G1-CA3 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 19No
b) 20A SP MCB 10KA = 5No
c) Spare Space = 6No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 18No
2.15 | DB-P1-G1-CA4 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 26No
b) 20A SP MCB 10KA = 9No
c) Spare Space = 10No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 22No
2.16 | DB-P1-G2-CA1 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 18No
b) 20A SP MCB 10KA = 6No
c) Spare Space = 9No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 16No
2.17 | DB-P1-G2-CA2 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 16No
b) 20A SP MCB 10KA = 3No
c) Spare Space = 8No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 15No
2.18 | DB-P1-G2-CA3 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 15No
b) 20A SP MCB 10KA = 11No
c) Spare Space = 10No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 14No
2.19 | DB-P1-G2-CA4 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 10No
b) 20A SP MCB 10KA = 6No
c) Spare Space = 8No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 10No
2.17 | DB-P1-1F-CA1 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 26No
b) 20A SP MCB 10KA = 5No
c) Spare Space = 11No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 24No
2.18 | DB-P1-1F-CA2 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 32No
b) 20A SP MCB 10KA = 6No
c) Spare Space = 13No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 26No
2.19 | DB-P1-2F-CA1 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 23No
b) 20A SP MCB 10KA = 4No
c) Spare Space = 10No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 20No
2.2 | DB-P1-2F-CA2 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 23No
b) 20A SP MCB 10KA = 5No
c) Spare Space = 5No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 20No
2.21 | DB-P1-2F-CA3 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 17No
b) 20A SP MCB 10KA = 2No
c) Spare Space = 5No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 17No
2.22 | DB-P1-2F-CA4 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 14No
b) 20A SP MCB 10KA = 2No
c) Spare Space = 5No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 14No
2.23 | DB-P1-2AF-CA1 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 25No
b) 20A SP MCB 10KA = 4No
c) Spare Space = 7No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 23No
2.24 | DB-P1-2AF-CA2 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 32No
b) 20A SP MCB 10KA = 7No
c) Spare Space = 6No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 29No
2.25 | DB-P1-2AF-CA3 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
Output Side:
a) 10A SP MCB 10KA = 16No
b) 20A SP MCB 10KA = 2No
c) Spare Space = 6No
d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 16No
TOTAL |  | PKR |  |  | 0
Note:
1) All the Distribution Boards (Floor Distribution Boards (FDB) & MSSB DB's) must have Voltmeter,Ammeter, Selector Switch, Phase Indication Lamps.
2) All the Distribution Boards (Comman Area (CA) DB's, Mechanical (ME) DB's, Fire Command Center (FCC) DB's)
must have Voltmeter, Selector Switch, Phase Indication Lamps.
3) Kindly Quote your final and Discounted rates for supply, Installation & Final Testing/Commissioning in all respect according to the BOQ items.
4) Do your value engineering as well and provide options if applicable and highlight those items as well, we will be obliged for your feedback.
5) If the items which you cannot provide please mention them as well in the BOQ.
6) Please study the schematic drawings as well as Specifications so that the items to be quoted must follow the specifications
7) Provide Technical specifications for all of the items mentioned in the BOQ or which you will add, and clearly highlight those item models

## BOQ for Mechanical Load DB's (hidden)
BOQ for Power Distribution System (Mechanical Load DB's)
for Basements, Ground-1 & 2, 1st, 2nd & 2A Floor for J7 Emporium Plot No: 1
S.No | Description | Unit | Qty | Supply Rate (PKR) | Supply Amount (PKR) | Remarks
A | LV Distribution Boards
2 | Mechanical Distribution Boards (ME)
Mechanical DBs (ME) shall be complied with BS EN 61349 with rating of 400V/230V 50Hz/ Water & Dust Proof of (IP42 Rating/Form 1/Wall Mounted (Non-Type Tested) Panels/ fabricated from 14 s.w.g sheet steel complete with hinged covers, the free end of which shall be secured by captive knurled thumb screws and chrome-plated lockable handle, gaskets, solid type concealed hinges, detachable undrilled end plates fitted top and bottom and external wall fixing lugs arranged to provide a small air gap between the back of the board and the wall. Including all related items e.g. MCBs/MCCBs/Phase Indication Lamps/Shunt trip Unit/Earth Leakage Relay with Toroid CT/ Energy Kwh Meters with BMS/EMS Compatability equipments required to complete the job in all respect as per Single Line Diagram (SLD) & specifictions.
2.1 | DB-P1-G1-ME1 & ME2 | Nos. | 2 |  | 0
Input Side:
a) 63 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
f) Space for Digital dual source Kwh Meter (DYN Rail Assembly) = 1No
g) Space for CT's for each Digital dual source Kwh Meter = 3No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 20A SP MCB 10KA = 1No
c) Spare Space (for 4P Breaker) = 1No
d) Spare Space (for SP Breaker) = 2No
2.2 | Isolators for G1 Floor:
| a) 100A Isolator | Nos. | 1
| b) 63A Isolator | Nos. | 1
2.3 | DB-P1-G2-ME1 & ME2 | Nos. | 2 |  | 0
Input Side:
a) 63 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
f) Space for Digital dual source Kwh Meter (DYN Rail Assembly) = 1No
g) Space for CT's for each Digital dual source Kwh Meter = 3No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 20A SP MCB 10KA = 1No
c) Spare Space (for 4P Breaker) = 1No
d) Spare Space (for SP Breaker) = 2No
2.4 | Isolators for G2 Floor:
| a) 63A Isolator | Nos. | 2
2.5 | DB-P1-1F-ME1 & ME2 | Nos. | 2 |  | 0
Input Side:
a) 63 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
f) Space for Digital dual source Kwh Meter (DYN Rail Assembly) = 1No
g) Space for CT's for each Digital dual source Kwh Meter = 3No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 20A SP MCB 10KA = 1No
c) Spare Space (for 4P Breaker) = 1No
d) Spare Space (for SP Breaker) = 2No
2.6 | Isolators for 1F Floor:
| a) 100A Isolator | Nos. | 2
2.7 | DB-P1-2F-ME1 | Nos. | 1 |  | 0
Input Side:
a) 40 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
f) Space for Digital dual source Kwh Meter (DYN Rail Assembly) = 1No
g) Space for CT's for each Digital dual source Kwh Meter = 3No
Output Side:
a) 40A 4P MCB 10KA = 1No
b) 20A SP MCB 10KA = 1No
c) Spare Space (for 4P Breaker) = 1No
d) Spare Space (for SP Breaker) = 2No
2.5 | DB-P1-2F-ME2 | Nos. | 1 |  | 0
Input Side:
a) 40 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
f) Space for Digital dual source Kwh Meter (DYN Rail Assembly) = 1No
g) Space for CT's for each Digital dual source Kwh Meter = 3No
Output Side:
a) 40A 4P MCB 10KA = 1No
b) 20A SP MCB 10KA = 2No
c) Spare Space (for 4P Breaker) = 1No
d) Spare Space (for SP Breaker) = 1No
2.6 | Isolators for 2F Floor:
| a) 100A Isolator | Nos. | 1
| b) 32A Isolator | Nos. | 1
2.6 | DB-P1-2AF-ME1 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
f) Space for Digital dual source Kwh Meter (DYN Rail Assembly) = 1No
g) Space for CT's for each Digital dual source Kwh Meter = 3No
Output Side:
a) 20A 4P MCB 10KA = 1No
b) 20A SP MCB 10KA = 2No
c) Spare Space (for 4P Breaker) = 1No
d) Spare Space (for SP Breaker) = 1No
2.7 | DB-P1-2AF-ME2 | Nos. | 1 |  | 0
Input Side:
a) 32 4P MCCB 10KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Phase Indication Lamps (R/Y/B) = 3No
d) Earth Leakage Relay with Toroide CT = 1No
e) Shunt Trip Unit = 1No
f) Space for Digital dual source Kwh Meter (DYN Rail Assembly) = 1No
g) Space for CT's for each Digital dual source Kwh Meter = 3No
Output Side:
a) 20A 4P MCB 10KA = 2No
b) 20A SP MCB 10KA = 1No
c) Spare Space (for 4P Breaker) = 1No
d) Spare Space (for SP Breaker) = 2No
2.6 | Isolators for 2AF Floor:
| a) 100A Isolator | Nos. | 2
TOTAL |  | PKR |  |  | 0
Note:
1) All the Distribution Boards (Floor Distribution Boards (FDB) & MSSB DB's) must have Voltmeter,Ammeter, Selector Switch, Phase Indication Lamps.
2) All the Distribution Boards (Comman Area (CA) DB's, Mechanical (ME) DB's, Fire Command Center (FCC) DB's)
must have Voltmeter, Selector Switch, Phase Indication Lamps.
3) Kindly Quote your final and Discounted rates for supply, Installation & Final Testing/Commissioning in all respect according to the BOQ items.
4) Do your value engineering as well and provide options if applicable and highlight those items as well, we will be obliged for your feedback.
5) If the items which you cannot provide please mention them as well in the BOQ.
6) Please study the schematic drawings as well as Specifications so that the items to be quoted must follow the specifications
7) Provide Technical specifications for all of the items mentioned in the BOQ or which you will add, and clearly highlight those item models

## Summary
CS for Power Distribution System (Common Area & Fire Command DB's)
for Ground-1 & 2, 1st, 2nd & 2A Floor for J7 Emporium Plot No: 1
DESCRIPTION |  |  |  | Vendor
Enclosure: Non Type-Tested
Breaker:
S.No | Description | Unit | Qty | Supply Rate | Amount | Remarks
A | LV Distribution Boards
Floor DBS |  |  |  | 0
CA DBS |  |  |  | 0
Mechanical DBS |  |  |  | 0
G Total LV DBs (FDB+CADB+MEDB) |  |  |  | 0
GST @ 17%: |  |  |  | 0
Total Amount (Including GST): |  |  |  | 0

## Sheet1 (hidden)
Vendor | Lineman | EARCON Group | IMS Electric | Bilal Engineering | Ravi Switchgear | Powertek Switchgear
G Total LV DBs (FDB+CADB+MEDB) | 14026543 | 0 | 11168000 | 10812250 | 0 | 11244990
GST @ 17%: | 2384512.31 | 0 | 1898560 | 1838082.5 | 0 | 1911648.3
Total Amount (Including GST): | 16411055.31 | 0 | 13066560 | 12650332.5 | 0 | 13156638.3

## FDBs
Power Distribution System (Floor DB's & Isolators)
for Ground-1 & 2, 1st, 2nd & 2A Floor for J7 Emporium Plot No: 1
DESCRIPTION |  |  |  | Vendor:
Enclosure: Non Type-Tested
Breaker:
S.No | Description | Unit | Qty | Supply Rate | Amount | Remarks
A | LV Distribution Boards
1 | Floor Distribution Boards (FDBs)
Floor DBs shall be complied with BS EN 61349 with rating of 400V/230V 50Hz/ Water & Dust Proof IP42 Rating / Form 2b/ Wall Mounted (Non-Type Tested) Panels/ fabricated from 14 s.w.g sheet steel complete with hinged covers, the free end of which shall be secured by captive knurled thumb screws and chrome-plated lockable handle, gaskets, solid type concealed hinges, detachable undrilled end plates fitted top and bottom and external wall fixing lugs arranged to provide a small air gap between the back of the board and the wall. Including all related items e.g. MCBs/MCCB/Volt Meters/Ameters/ Selectors switches/Phase Indication Lamps/ Shunt trip Unit/Earth Leakage Relay with Toroid CT/ CTs/ Energy Kwh Meters with BMS/EMS Compatability and any other related equipments required to complete the job in all respect as per Single Line Diagram (SLD) & specifictions.
1.1 | Ground-1 Floor:
1.1.a | FDB-P1-G1-1 | Nos. | 1 |  | 0
Input Side:
a) 630AF/630AT Adj. 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 600A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 40A 4P MCB 10KA = 1No
c) 32A 4P MCB 10KA = 16No
d) Spare Space = 2No
e) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 13No
1.1.b | FDB-P1-G1-2 | Nos. | 1 |  | 0
Input Side:
a) 630AF/630AT Adj. 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 600A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 32A 4P MCB 10KA = 15No
c) Spare Space = 2No
d) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 13No
1.1.c | Isolators for G1 Floor:
| a) 40A Isolator | Nos. | 1 |  | 0
| b) 32A Isolator | Nos. | 27 |  | 0
TOTAL (Ground-1 Floor) |  | PKR
1.2 | Ground-2 Floor:
1.2.a | FDB-P1-G2-1 | Nos. | 1 |  | 0
Input Side:
a) 400AF/400AT Adj. 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 400A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 150A 4P MCB 18KA = 1No
b) 63A 4P MCB 10KA = 1No
c) 32A 4P MCB 10KA = 13No
d) Spare Space = 2No
e) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 11No
f) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) with CTs more than 100Amps = 1No
g) Space for CT's for Digital dual source Kwh Meter = 3No
1.2.b | FDB-P1-G2-2 | Nos. | 1 |  | 0
Input Side:
a) 630AF/630AT Adj. 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 600A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 40A 4P MCB 10KA = 2No
c) 32A 4P MCB 10KA = 16No
d) Spare Space = 3No
e) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 14No
1.2.c | Isolators for G2 Floor:
| a) 150A Isolator | Nos. | 1 |  | 0
| b) 40A Isolator | Nos. | 2 |  | 0
| c) 32A Isolator | Nos. | 25 |  | 0
TOTAL (Ground-2 Floor) |  | PKR
1.3 | 1st Floor:
1.3.a | FDB-P1-1F-1 | Nos. | 1 |  | 0
Input Side:
a) 400AF/400AT Adj. 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 400A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 32A 4P MCB 10KA = 14No
c) Spare Space = 2No
d) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 13No
1.3.b | FDB-P1-1F-2 | Nos. | 1 |  | 0
Input Side:
a) 400AF/400AT Adj. 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 400A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 32A 4P MCB 10KA = 13No
c) Spare Space = 2No
d) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 10No
1.3.c | Isolators for 1F Floor:
| a) 32A Isolator | Nos. | 25 |  | 0
TOTAL (1st Floor) |  | PKR
1.4 | 2nd Floor:
1.4.a | FDB-P1-2F-1 | Nos. | 1 |  | 0
Input Side:
a) 250AF/250AT Adj. 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 250A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 40A 4P MCB 10KA = 1No
b) 32A 4P MCB 10KA = 12No
c) Spare Space = 2No
d) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 10No
1.4.b | FDB-P1-2F-2 | Nos. | 1 |  | 0
Input Side:
a) 250AF/250AT Adj. 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 250A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 63A 4P MCB 10KA = 1No
b) 40A 4P MCB 10KA = 2No
c) 32A 4P MCB 10KA = 10No
d) Spare Space = 2No
e) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 8No
1.4.c | Isolators for 2F Floor:
| a) 63A Isolator | Nos. | 1 |  | 0
| b) 40A Isolator | Nos. | 2 |  | 0
| c) 32A Isolator | Nos. | 17 |  | 0
TOTAL (2nd Floor) |  | PKR
1.5 | 2A Floor:
1.5.a | FDB-P1-2AF-1 | Nos. | 1 |  | 0
Input Side:
a) 250AF/250AT Adj. 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 250A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 32A 4P MCB 10KA = 13No
b) Spare Space = 2No
c) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 10No
1.5.b | FDB-P1-2AF-2 | Nos. | 1 |  | 0
Input Side:
a) 250AF/250AT Adj. 4P MCCB 36KA = 1No
b) 2A SP 6KA Control Circuit Breaker = 3No
c) Voltmeter with Selector Switch = 1No
d) Ammeter = 1No
e) Phase Indication Lamps (R/Y/B) = 3No
f) CT's 250A/5A = 3No
g) Earth Leakage Relay with Toroide CT = 1No
h) Shunt Trip Unit = 1No
Output Side:
a) 160A 4P MCB 18KA = 1No
b) 63A 4P MCB 10KA = 1No
c) 40A 4P MCB 10KA = 2No
d) 32A 4P MCB 10KA = 7No
e) Spare Space = 2No
f) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) without CTs upto 80Amps = 6No
g) Space for Digital dual source Kwh Meter (Direct Measurement, DYN Rail Assembly) with CTs above 100Amps = 1No
h) Space for CT's for each Digital dual source Kwh Meter = 3No
1.5.c | Isolators for 2AF Floor:
| a) 160A Isolator | Nos. | 1 |  | 0
| b) 63A Isolator | Nos. | 1 |  | 0
| c) 40A Isolator | Nos. | 2 |  | 0
| d) 32A Isolator | Nos. | 15 |  | 0
G Total Floor DBs |  |  |  | 0
GST @ 17%: |  |  |  | 0
Total Amount (Including GST): |  |  |  | 0

## CA & FCC DBs
Power Distribution System (Common Area & Fire Command DB's)
for Ground-1 & 2, 1st, 2nd & 2A Floor for J7 Emporium Plot No: 1
DESCRIPTION |  |  |  | Vendor
Enclosure: Non Type-Tested
Breaker:
S.No | Description | Unit | Qty | Supply Rate | Amount | Remarks
A | LV Distribution Boards
2 | Common Area & Fire Command Centre Distribution Boards (CA & FCC)
Comman Area & Fire Command Center DBs shall be complied with BS EN 61349 with rating of 400V/230V 50Hz/ Water & Dust Proof of (IP42 Rating/Form 1/Wall Mounted (Non-Type Tested) Panels/ fabricated from 14 s.w.g sheet steel complete with hinged covers, the free end of which shall be secured by captive knurled thumb screws and chrome-plated lockable handle, gaskets, solid type concealed hinges, detachable undrilled end plates fitted top and bottom and external wall fixing lugs arranged to provide a small air gap between the back of the board and the wall. Including all related items e.g. MCBs/MCCBs/Phase Indication Lamps/Shunt trip Unit/Earth Leakage Relay with Toroid CT/Relay Modules with BMS/EMS Compatability and any other related equipments required to complete the job in all respect as per Single Line Diagram (SLD) & specifictions.
2.1 | Ground-1 Floor:
2.1.a | DB-P1-G1-CA1 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 27No |  |  |  | 0
| b) 20A SP MCB 10KA = 4No |  |  |  | 0
| c) Spare Space = 8No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 25No |  |  |  | 0
2.1.b | DB-P1-G1-CA2 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 17No |  |  |  | 0
| b) 20A SP MCB 10KA = 2No |  |  |  | 0
| c) Spare Space = 5No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 16No |  |  |  | 0
2.1.c | DB-P1-G1-CA3 (Concealed inside wall with Max. 150mm depth) | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 19No |  |  |  | 0
| b) 20A SP MCB 10KA = 5No |  |  |  | 0
| c) Spare Space = 6No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 18No |  |  |  | 0
2.1.d | DB-P1-G1-CA4 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 26No |  |  |  | 0
| b) 20A SP MCB 10KA = 9No |  |  |  | 0
| c) Spare Space = 10No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 22No |  |  |  | 0
TOTAL (Ground-1 Floor) |  | PKR
2.2 | Ground-2 Floor:
2.2.a | DB-P1-G2-CA1 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 18No |  |  |  | 0
| b) 20A SP MCB 10KA = 6No |  |  |  | 0
| c) Spare Space = 9No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 16No |  |  |  | 0
2.2.b | DB-P1-G2-CA2 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 16No |  |  |  | 0
| b) 20A SP MCB 10KA = 3No |  |  |  | 0
| c) Spare Space = 8No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 15No |  |  |  | 0
2.2.c | DB-P1-G2-CA3 (Concealed inside wall with Max. 150mm depth) | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 15No |  |  |  | 0
| b) 20A SP MCB 10KA = 11No |  |  |  | 0
| c) Spare Space = 10No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 14No |  |  |  | 0
2.2.d | DB-P1-G2-CA4 (Concealed inside wall with Max. 150mm depth) | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 10No |  |  |  | 0
| b) 20A SP MCB 10KA = 6No |  |  |  | 0
| c) Spare Space = 8No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 10No |  |  |  | 0
2.2.e | DB-P1-G2-FCC (Fire Command Centre DB) | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 2P MCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 1No |  |  |  | 0
| c) Phase Indication Lamps (R) = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 1No |  |  |  | 0
| b) 20A SP MCB 10KA = 3No |  |  |  | 0
| c) Spare Space = 2No |  |  |  | 0
TOTAL (Ground-2 Floor) |  | PKR
2.3 | 1st Floor:
2.3.a | DB-P1-1F-CA1 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 26No |  |  |  | 0
| b) 20A SP MCB 10KA = 5No |  |  |  | 0
| c) Spare Space = 11No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 24No |  |  |  | 0
2.3.b | DB-P1-1F-CA2 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 32No |  |  |  | 0
| b) 20A SP MCB 10KA = 6No |  |  |  | 0
| c) Spare Space = 13No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 26No |  |  |  | 0
TOTAL (1st Floor) |  | PKR
2.4 | 2nd Floor:
2.4.a | DB-P1-2F-CA1 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 23No |  |  |  | 0
| b) 20A SP MCB 10KA = 4No |  |  |  | 0
| c) Spare Space = 10No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 20No |  |  |  | 0
2.4.b | DB-P1-2F-CA2 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 23No |  |  |  | 0
| b) 20A SP MCB 10KA = 5No |  |  |  | 0
| c) Spare Space = 5No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 20No |  |  |  | 0
2.4.c | DB-P1-2F-CA3 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 17No |  |  |  | 0
| b) 20A SP MCB 10KA = 2No |  |  |  | 0
| c) Spare Space = 5No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 17No |  |  |  | 0
2.4.d | DB-P1-2F-CA4 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 14No |  |  |  | 0
| b) 20A SP MCB 10KA = 2No |  |  |  | 0
| c) Spare Space = 5No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 14No |  |  |  | 0
TOTAL (2nd Floor) |  | PKR
2.5 | 2A Floor:
2.5.a | DB-P1-2AF-CA1 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 25No |  |  |  | 0
| b) 20A SP MCB 10KA = 4No |  |  |  | 0
| c) Spare Space = 7No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 23No |  |  |  | 0
2.5.b | DB-P1-2AF-CA2 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 32No |  |  |  | 0
| b) 20A SP MCB 10KA = 7No |  |  |  | 0
| c) Spare Space = 6No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 29No |  |  |  | 0
2.5.c | DB-P1-2AF-CA3 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 10A SP MCB 10KA = 16No |  |  |  | 0
| b) 20A SP MCB 10KA = 2No |  |  |  | 0
| c) Spare Space = 6No |  |  |  | 0
| d) Impulse Relay Module 1P 10A comptable with BMS/EMS with protocals BACnet RS-485 network = 16No |  |  |  | 0
G Total CA DBs |  |  |  | 0
GST @ 17%: |  |  |  | 0
Total Amount (Including GST): |  |  |  | 0

## Mechanical Load DB's
Power Distribution System (Mechanical Load DB's)
for Ground-1 & 2, 1st, 2nd & 2A Floor for J7 Emporium Plot No: 1
DESCRIPTION |  |  |  | Vendor
Enclosure: Non Type-Tested
Breaker: Schnieder
S.No | Description | Unit | Qty | Supply Rate | Amount | Remarks
A | LV Distribution Boards
3 | Mechanical Distribution Boards (ME)
Mechanical DBs (ME) shall be complied with BS EN 61349 with rating of 400V/230V 50Hz/ Water & Dust Proof of (IP42 Rating/Form 1/Wall Mounted (Non-Type Tested) Panels/ fabricated from 14 s.w.g sheet steel complete with hinged covers, the free end of which shall be secured by captive knurled thumb screws and chrome-plated lockable handle, gaskets, solid type concealed hinges, detachable undrilled end plates fitted top and bottom and external wall fixing lugs arranged to provide a small air gap between the back of the board and the wall. Including all related items e.g. MCBs/MCCBs/Phase Indication Lamps/Shunt trip Unit/Earth Leakage Relay with Toroid CT/ Power Analyzer with BMS/EMS Compatability equipments required to complete the job in all respect as per Single Line Diagram (SLD) & specifictions.
3.1 | Ground-1 Floor:
3.1a | DB-P1-G1-ME1 & ME2 | Nos. | 2 |  | 0
| Input Side: |  |  |  | 0
| a) 63 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| f) Digital Power Analyzer = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 63A 4P MCB 10KA = 1No |  |  |  | 0
| b) 20A SP MCB 10KA = 1No |  |  |  | 0
| c) Spare Space (for 4P Breaker) = 1No |  |  |  | 0
| d) Spare Space (for SP Breaker) = 2No |  |  |  | 0
3.1b | Isolators for G1 Floor: |  |  |  | 0
| a) 100A Isolator | Nos. | 1 |  | 0
| b) 63A Isolator | Nos. | 1 |  | 0
TOTAL (Ground-1 Floor) |  | PKR
3.2 | Ground-2 Floor:
3.2a | DB-P1-G2-ME1 & ME2 | Nos. | 2 |  | 0
| Input Side: |  |  |  | 0
| a) 63 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| f) Digital Power Analyzer = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 63A 4P MCB 10KA = 1No |  |  |  | 0
| b) 20A SP MCB 10KA = 1No |  |  |  | 0
| c) Spare Space (for 4P Breaker) = 1No |  |  |  | 0
| d) Spare Space (for SP Breaker) = 2No |  |  |  | 0
3.2b | Isolators for G2 Floor: |  |  |  | 0
| a) 63A Isolator | Nos. | 2 |  | 0
TOTAL (Ground-2 Floor) |  | PKR
3.3 | 1st Floor:
3.3a | DB-P1-1F-ME1 & ME2 | Nos. | 2 |  | 0
| Input Side: |  |  |  | 0
| a) 63 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| f) Digital Power Analyzer = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 63A 4P MCB 10KA = 1No |  |  |  | 0
| b) 20A SP MCB 10KA = 1No |  |  |  | 0
| c) Spare Space (for 4P Breaker) = 1No |  |  |  | 0
| d) Spare Space (for SP Breaker) = 2No |  |  |  | 0
3.3b | Isolators for 1F Floor: |  |  |  | 0
| a) 100A Isolator | Nos. | 2 |  | 0
TOTAL (1st Floor) |  | PKR
3.4 | 2nd Floor:
3.4a | DB-P1-2F-ME1 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 40 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| f) Digital Power Analyzer = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 40A 4P MCB 10KA = 1No |  |  |  | 0
| b) 20A SP MCB 10KA = 1No |  |  |  | 0
| c) Spare Space (for 4P Breaker) = 1No |  |  |  | 0
| d) Spare Space (for SP Breaker) = 2No |  |  |  | 0
3.4b | DB-P1-2F-ME2 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 40 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| f) Digital Power Analyzer = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 40A 4P MCB 10KA = 1No |  |  |  | 0
| b) 20A SP MCB 10KA = 2No |  |  |  | 0
| c) Spare Space (for 4P Breaker) = 1No |  |  |  | 0
| d) Spare Space (for SP Breaker) = 1No |  |  |  | 0
3.4c | Isolators for 2F Floor: |  |  |  | 0
| a) 100A Isolator | Nos. | 1 |  | 0
| b) 32A Isolator | Nos. | 1 |  | 0
TOTAL (2nd Floor) |  | PKR
3.5 | 2A Floor:
3.5a | DB-P1-2AF-ME1 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| f) Digital Power Analyzer = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 20A 4P MCB 10KA = 1No |  |  |  | 0
| b) 20A SP MCB 10KA = 2No |  |  |  | 0
| c) Spare Space (for 4P Breaker) = 1No |  |  |  | 0
| d) Spare Space (for SP Breaker) = 1No |  |  |  | 0
3.5b | DB-P1-2AF-ME2 | Nos. | 1 |  | 0
| Input Side: |  |  |  | 0
| a) 32 4P MCCB 10KA = 1No |  |  |  | 0
| b) 2A SP 6KA Control Circuit Breaker = 3No |  |  |  | 0
| c) Phase Indication Lamps (R/Y/B) = 3No |  |  |  | 0
| d) Earth Leakage Relay with Toroide CT = 1No |  |  |  | 0
| e) Shunt Trip Unit = 1No |  |  |  | 0
| f) Digital Power Analyzer = 1No |  |  |  | 0
| Output Side: |  |  |  | 0
| a) 20A 4P MCB 10KA = 2No |  |  |  | 0
| b) 20A SP MCB 10KA = 1No |  |  |  | 0
| c) Spare Space (for 4P Breaker) = 1No |  |  |  | 0
| d) Spare Space (for SP Breaker) = 2No |  |  |  | 0
3.5c | Isolators for 2AF Floor: |  |  |  | 0
| a) 100A Isolator | Nos. | 2 |  | 0
G Total Mechnical DBs |  |  |  | 0
GST @ 17%: |  |  |  | 0
Total Amount (Including GST): |  |  |  | 0