## LV System (Plot-1 & 2)
J7 EMPORIUM
ENGINEERING DIVISION
BOQ FOR TOTAL LV SYSTEM (Emporium Plot-1 & 2) Type Tested
Description |  |  |  | Vendor
Enclosure: Type-Tested
Breaker:
Sr. No | Item Description | Unit | Req: Qty | Supply Rate | Amount | Remarks
1 | LV Panels (Emporium Plot-1) Podium-1
1.1 | MDB-P1-1 & MDB-P1-2 (For Podium-1 Chillers rating 400V): | Nos | S
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 2500 AT/AF 4P Adj. ACB Breaker = 1No.
b) 1600 AT/AF 4P Adj. ACB Breaker = 1No.
c) 630 AT/AF 4P Adj. MCCB Breaker = 1No.
d) 400 AT/AF 4P Adj. MCCB Breaker = 1No.
e) 160 AT/AF 4P Adj. MCCB Breaker = 2No.
f) with spare space for future = 2No.
g) Power Factor Correction Panel (850 kVAR with detuned Reactor = 100kVAR x 7 Steps + 50kVAR x 3 Steps) = 1No.
h) Energy (kWH) Meters comptable with BMS System = 5No
i) Including other related Accessories as per SLD.
1.2 | MDB-P1-3 & MDB-P1-4 (For Podium-1 General Loads rating 400V): | Nos | 2 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 1600 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) with spare space for future = 2No.
d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No.
e) Energy (kWH) Meters comptable with BMS System = 2No
f) Including other related Accessories as per SLD.
1.3 | LSDB-P1-1 (For Podium-1 Life safety DB for Mech-Load rating 400V): | Nos | 1 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 800A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 800 AT/AF 4P Adj. MCCB Breaker MA Type = 1No.
b) Energy (kWH) Meters comptable with BMS System = 1No.
c) 800A ATS = 1No.
d) Including other related Accessories as per SLD.
Outgoing Side:
a) 160A 4P MCCB Breaker MA Type = 1No.
b) 63A 4P MCCB Breaker MA Type = 10No
c) 40A 4P MCCB Breaker MA Type = 1No
d) 32A 4P MCCB Breaker MA Type = 2No
e) with spare space for future = 2No.
f) Energy (kWH) Meters comptable with BMS System = 14No
g) Including other related Accessories as per SLD.
LV Panels (Emporium Plot-1) Tower-1 & 2
1.4 | MDB-P1-5 (For Plot-1 Tower-1 rating 400V): | Nos | 1 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 1600 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) with spare space for future = 2No.
d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No.
e) Energy (kWH) Meters comptable with BMS System = 2No
f) Including other related Accessories as per SLD.
1.5 | MDB-P1-6 (For Plot-1 Tower-2 rating 400V): | Nos | 1 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 2500 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) 1000 AT/AF 4P Adj. MCCB Breaker = 1No
d) 400 AT/AF 4P Adj. MCCB Breaker = 1No
e) with spare space for future = 2No.
f) Power Factor Correction Panel (750 kVAR with detuned Reactor = 75kVAR x 9 Steps + 25kVAR x 3 Steps) = 1No.
g) Energy (kWH) Meters comptable with BMS System = 4No
h) Including other related Accessories as per SLD.
1.6 | LSDB-P1-2 (For Tower-1&2 Life safety DB for Mech-Load rating 400V): | Nos | 1 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 400A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 400 AT/AF 4P Adj. MCCB Breaker MA Type = 1No.
b) Energy (kWH) Meters comptable with BMS System = 1No.
c) 400A ATS = 1No.
d) Including other related Accessories as per SLD.
Outgoing Side:
a) 160A 4P MCCB Breaker MA Type = 2No.
b) 40A 4P MCCB Breaker MA Type = 1No
c) with spare space for future = 2No.
d) Energy (kWH) Meters comptable with BMS System = 3No
e) Including other related Accessories as per SLD.
Total LV Panels (Emporium Plot-1) (Podium-1, Tower 1 & 2) Exclusive of 17% GST |  |  |  | 0
17% GST |  |  |  | 0
G.Total LV Panels (Emporium Plot-1) (Podium-1, Tower 1 & 2) Inclusive of 17% GST |  |  |  | 0
2 | LV Panels (Emporium Plot-2) Podium-2
2.1 | MDB-P2-1 (For Podium-2 Chillers rating 400V): | Nos | 1 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 2500 AT/AF 4P Adj. ACB Breaker = 1No.
b) 1600 AT/AF 4P Adj. ACB Breaker = 1No.
c) 250 AT/AF 4P Adj. MCCB Breaker = 2No.
d) 160 AT/AF 4P Adj. MCCB Breaker = 2No.
e) with spare space for future = 2No.
f) Power Factor Correction Panel (850 kVAR with detuned Reactor = 100kVAR x 7 Steps + 50kVAR x 3 Steps) = 1No.
g) Energy (kWH) Meters comptable with BMS System = 5No
h) Including other related Accessories as per SLD.
2.2 | MDB-P2-2 (For Podium-2 Chillers rating 400V): | Nos | 1 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 1600 AT/AF 4P Adj. ACB Breaker = 2No.
b) 630 AT/AF 4P Adj. MCCB Breaker = 1No
c) 400 AT/AF 4P Adj. MCCB Breaker = 1No.
d) 160 AT/AF 4P Adj. MCCB Breaker = 2No.
e) with spare space for future = 2No.
f) Power Factor Correction Panel (850 kVAR with detuned Reactor = 100kVAR x 7 Steps + 50kVAR x 3 Steps) = 1No.
g) Energy (kWH) Meters comptable with BMS System = 5No
h) Including other related Accessories as per SLD.
2.3 | MDB-P2-3 & MDB-P2-4 (For Podium-2 General Loads rating 400V): | Nos | 2 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 1600 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) with spare space for future = 2No.
d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No.
e) Energy (kWH) Meters comptable with BMS System = 2No
f) Including other related Accessories as per SLD.
2.4 | LSDB-P2-1 (For Podium-2 Life safety DB for Mech-Load rating 400V): | Nos | 1 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 800A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 800 AT/AF 4P Adj. MCCB Breaker MA Type = 1No.
b) Energy (kWH) Meters comptable with BMS System = 1No.
c) 800A ATS = 1No.
d) Including other related Accessories as per SLD.
Outgoing Side:
a) 160A 4P MCCB Breaker MA Type = 1No.
b) 63A 4P MCCB Breaker MA Type = 10No
c) 40A 4P MCCB Breaker MA Type = 1No
d) 32A 4P MCCB Breaker MA Type = 1No
e) with spare space for future = 2No.
f) Energy (kWH) Meters comptable with BMS System = 13No
g) Including other related Accessories as per SLD.
(Emporium Plot-2) Tower-1 & 2
2.5 | MDB-P2-5 (For Plot-2 Tower-1 rating 400V): | Nos | 1 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 2500 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) with spare space for future = 2No.
d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No.
e) Energy (kWH) Meters comptable with BMS System = 2No
f) Including other related Accessories as per SLD.
2.6 | MDB-P2-6 (For Plot-2 Tower-2 rating 400V): | Nos | 1 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 2500 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) 1000 AT/AF 4P Adj. MCCB Breaker = 1No
d) 400 AT/AF 4P Adj. MCCB Breaker = 1No
e) with spare space for future = 2No.
f) Power Factor Correction Panel (750 kVAR with detuned Reactor = 75kVAR x 9 Steps + 25kVAR x 3 Steps) = 1No.
g) Energy (kWH) Meters comptable with BMS System = 4No
h) Including other related Accessories as per SLD.
2.7 | LSDB-P2-2 (For Tower-1&2 Life safety DB for Mech-Load rating 400V): | Nos | 1 |  | 0
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 400A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 400 AT/AF 4P Adj. MCCB Breaker MA Type = 1No.
b) Energy (kWH) Meters comptable with BMS System = 1No.
c) 400A ATS = 1No.
d) Including other related Accessories as per SLD.
Outgoing Side:
a) 160A 4P MCCB Breaker MA Type = 2No.
b) 40A 4P MCCB Breaker MA Type = 1No
c) with spare space for future = 2No.
d) Energy (kWH) Meters comptable with BMS System = 3No
e) Including other related Accessories as per SLD.
Total LV Panels (Emporium Plot-2) (Podium-2, Tower 1 & 2) Exclusive of 17% GST |  |  |  | 0
17% GST |  |  |  | 0
G.Total LV Panels (Emporium Plot-1) (Podium-1, Tower 1 & 2) Inclusive of 17% GST |  |  |  | 0
Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Exclusive of 17% GST |  |  |  | 0
17% GST |  |  |  | 0
G.Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Inclusive of 17% GST |  |  |  | 0

## Non Type Tested (hidden)
J7 EMPORIUM
ENGINEERING DIVISION
BOQ FOR TOTAL LV SYSTEM (Emporium Plot-1 & 2) Non Type Tested
Description |  |  |  | Siemens Energy |  |  | Schneider Electric (Type Tested) |  |  | EARCON Group (Non-Type tested) (old Quote) |  |  | IMS |  |  | Bilal Engineering (Pvt.) Ltd |  |  | Ravi Switchgear
|  |  |  | Enclosure: Non Type Tested |  |  | Enclosure: Non Type Tested |  |  | Enclosure: Non-Type Tested |  |  | Enclosure: Non Type Tested |  |  | Enclosure: Type Tested |  |  | Enclosure: Non Type Tested
|  |  |  | Breaker: Siemens |  |  | Breaker: Schneider |  |  | Breaker: ABB |  |  | Breaker:Schneider (Europe) |  |  | Breaker: ABB |  |  | Breaker:Schneider (Europe)
Sr. No | Item Description | Unit | Req: Qty | Supply Rate | Amount | Remarks | Supply Rate | Amount | Remarks | Supply Rate | Amount | Remarks | Supply Rate | Amount | Remarks | Supply Rate | Amount | Remarks | Supply Rate | Amount | Remarks
1 | LV Panels (Emporium Plot-1) Podium-1
1.1 | MDB-P1-1 & MDB-P1-2 (For Podium-1 Chillers rating 400V): | Nos | 2 |  | 0 |  |  | 0 |  |  | 0 |  | 20618900 | 41237800 |  | 20384565 | 40769130 | both DBs has different prices so that's why the average price of both is taken | 20143126.5 | 40286253 | both DBs has different prices so that's why the average price of both is taken
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 2500 AT/AF 4P Adj. ACB Breaker = 1No.
b) 1600 AT/AF 4P Adj. ACB Breaker = 1No.
c) 630 AT/AF 4P Adj. MCCB Breaker = 1No.
d) 400 AT/AF 4P Adj. MCCB Breaker = 1No.
e) 160 AT/AF 4P Adj. MCCB Breaker = 2No.
f) with spare space for future = 2No.
g) Power Factor Correction Panel (850 kVAR with detuned Reactor = 100kVAR x 7 Steps + 50kVAR x 3 Steps) = 1No.
h) Energy (kWH) Meters comptable with BMS System = 5No
i) Including other related Accessories as per SLD.
1.2 | MDB-P1-3 & MDB-P1-4 (For Podium-1 General Loads rating 400V): | Nos | 2 |  | 0 |  |  | 0 |  |  | 0 |  | 16949870 | 33899740 |  | 18054995 | 36109990 | both DBs has different prices so that's why the average price of both is taken | 16223516 | 32447032
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 1600 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) with spare space for future = 2No.
d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No.
e) Energy (kWH) Meters comptable with BMS System = 2No
f) Including other related Accessories as per SLD.
1.3 | LSDB-P1-1 (For Podium-1 Life safety DB for Mech-Load rating 400V): | Nos | 1 |  | 0 |  |  | 0 |  |  | 0 |  | 10583370 | 10583370 |  | 6050550 | 6050550 |  | 6025944 | 6025944
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 800A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 800 AT/AF 4P Adj. MCCB Breaker MA Type = 1No.
b) Energy (kWH) Meters comptable with BMS System = 1No.
c) 800A ATS = 1No.
d) Including other related Accessories as per SLD.
Outgoing Side:
a) 160A 4P MCCB Breaker MA Type = 1No.
b) 63A 4P MCCB Breaker MA Type = 10No
c) 40A 4P MCCB Breaker MA Type = 1No
d) 32A 4P MCCB Breaker MA Type = 2No
e) with spare space for future = 2No.
f) Energy (kWH) Meters comptable with BMS System = 14No
g) Including other related Accessories as per SLD.
LV Panels (Emporium Plot-1) Tower-1 & 2
1.4 | MDB-P1-5 (For Plot-1 Tower-1 rating 400V): | Nos | 1 |  | 0 |  |  | 0 |  |  | 0 |  | 17787680 | 17787680 |  | 15764840 | 15764840 |  | 16106683 | 16106683
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 1600 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) with spare space for future = 2No.
d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No.
e) Energy (kWH) Meters comptable with BMS System = 2No
f) Including other related Accessories as per SLD.
1.5 | MDB-P1-6 (For Plot-1 Tower-2 rating 400V): | Nos | 1 |  | 0 |  |  | 0 |  |  | 0 |  | 20608200 | 20608200 |  | 22958840 | 22958840 |  | 21125526 | 21125526
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 2500 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) 1000 AT/AF 4P Adj. MCCB Breaker = 1No
d) 400 AT/AF 4P Adj. MCCB Breaker = 1No
e) with spare space for future = 2No.
f) Power Factor Correction Panel (750 kVAR with detuned Reactor = 75kVAR x 9 Steps + 25kVAR x 3 Steps) = 1No.
g) Energy (kWH) Meters comptable with BMS System = 4No
h) Including other related Accessories as per SLD.
1.6 | LSDB-P1-2 (For Tower-1&2 Life safety DB for Mech-Load rating 400V): | Nos | 1 |  | 0 |  |  | 0 |  |  | 0 |  | 4003940 | 4003940 |  | 2789140 | 2789140 | LSDB-P1-2 didi not find only remaning of all the name was LSDB-P1-1 (Tower) | 2433589 | 2433589
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 400A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 400 AT/AF 4P Adj. MCCB Breaker MA Type = 1No.
b) Energy (kWH) Meters comptable with BMS System = 1No.
c) 400A ATS = 1No.
d) Including other related Accessories as per SLD.
Outgoing Side:
a) 160A 4P MCCB Breaker MA Type = 2No.
b) 40A 4P MCCB Breaker MA Type = 1No
c) with spare space for future = 2No.
d) Energy (kWH) Meters comptable with BMS System = 3No
e) Including other related Accessories as per SLD.
Total LV Panels (Emporium Plot-1) (Podium-1, Tower 1 & 2) Exclusive of 17% GST |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 128120730 |  |  | 124442490 |  |  | 118425027
Total LV Panels (Emporium Plot-1) (Podium-1, Tower 1 & 2) Inclusive of 17% GST |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 21780524.1 |  |  | 21155223.3 |  |  | 20132254.59
G.Total LV Panels (Emporium Plot-1) (Podium-1, Tower 1 & 2) Inclusive of 17% GST |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 149901254.1 |  |  | 145597713.3 |  |  | 138557281.59
2 | LV Panels (Emporium Plot-2) Podium-2
2.1 | MDB-P2-1 (For Podium-2 Chillers rating 400V): | Nos | 1 |  | 0 |  |  | 0 |  |  | 0 |  | 19673000 | 19673000 |  | 17704090 | 17704090 |  | 18209498 | 18209498
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 2500 AT/AF 4P Adj. ACB Breaker = 1No.
b) 1600 AT/AF 4P Adj. ACB Breaker = 1No.
c) 250 AT/AF 4P Adj. MCCB Breaker = 2No.
d) 160 AT/AF 4P Adj. MCCB Breaker = 2No.
e) with spare space for future = 2No.
f) Power Factor Correction Panel (850 kVAR with detuned Reactor = 100kVAR x 7 Steps + 50kVAR x 3 Steps) = 1No.
g) Energy (kWH) Meters comptable with BMS System = 5No
h) Including other related Accessories as per SLD.
2.2 | MDB-P2-2 (For Podium-2 Chillers rating 400V): | Nos | 1 |  | 0 |  |  | 0 |  |  | 0 |  | 19064190 | 19064190 |  | 22238750 | 22238750 |  | 20822141 | 20822141
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 1600 AT/AF 4P Adj. ACB Breaker = 2No.
b) 630 AT/AF 4P Adj. MCCB Breaker = 1No
c) 400 AT/AF 4P Adj. MCCB Breaker = 1No.
d) 160 AT/AF 4P Adj. MCCB Breaker = 2No.
e) with spare space for future = 2No.
f) Power Factor Correction Panel (850 kVAR with detuned Reactor = 100kVAR x 7 Steps + 50kVAR x 3 Steps) = 1No.
g) Energy (kWH) Meters comptable with BMS System = 5No
h) Including other related Accessories as per SLD.
2.3 | MDB-P2-3 & MDB-P2-4 (For Podium-2 General Loads rating 400V): | Nos | 2 |  | 0 |  |  | 0 |  |  | 0 |  | 16894230 | 33788460 |  | 18054995 | 36109990 | both DBs has different prices so that's why the average price of both is taken | 16263092.5 | 32526185
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 1600 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) with spare space for future = 2No.
d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No.
e) Energy (kWH) Meters comptable with BMS System = 2No
f) Including other related Accessories as per SLD.
2.4 | LSDB-P2-1 (For Podium-2 Life safety DB for Mech-Load rating 400V): | Nos | 1 |  | 0 |  |  | 0 |  |  | 0 |  | 10342620 | 10342620 |  | 5899150 | 5899150 |  | 6025944 | 6025944
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 800A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 800 AT/AF 4P Adj. MCCB Breaker MA Type = 1No.
b) Energy (kWH) Meters comptable with BMS System = 1No.
c) 800A ATS = 1No.
d) Including other related Accessories as per SLD.
Outgoing Side:
a) 160A 4P MCCB Breaker MA Type = 1No.
b) 63A 4P MCCB Breaker MA Type = 10No
c) 40A 4P MCCB Breaker MA Type = 1No
d) 32A 4P MCCB Breaker MA Type = 1No
e) with spare space for future = 2No.
f) Energy (kWH) Meters comptable with BMS System = 13No
g) Including other related Accessories as per SLD.
(Emporium Plot-2) Tower-1 & 2
2.5 | MDB-P2-5 (For Plot-2 Tower-1 rating 400V): | Nos | 1 |  | 0 |  |  | 0 |  |  | 0 |  | 17787680 | 17787680 |  | 15764840 | 15764840 |  | 16106683 | 16106683
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 2500 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) with spare space for future = 2No.
d) Power Factor Correction Panel (650 kVAR with detuned Reactor = 75kVAR x 8 Steps + 25kVAR x 2 Steps) = 1No.
e) Energy (kWH) Meters comptable with BMS System = 2No
f) Including other related Accessories as per SLD.
2.6 | MDB-P2-6 (For Plot-2 Tower-2 rating 400V): | Nos | 1 |  | 0 |  |  | 0 |  |  | 0 |  | 20608200 | 20608200 |  | 22958840 | 22958840 |  | 21125526 | 21125526
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 3200A 4P Cooper Busbar 65kA for 1 sec with E&M Interlock/Form 4B/IP21 including Protection Relays: Under/Over Voltage Relay, Earth Fault Relay, Earth Leakage Relay, Phase Failure Relay, Shunt Trip Unit, Automatic Power Factor Correction Relay, Surge Protection Devices, Digital Power Analyzers for measuring (V,A,KVA,kVAR, P.F) & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 3200 AT/AF 4P Adj. ACB Breaker = 1No.
b) Digital Power Analyzers comptable with BMS System = 1No.
c) Including other related Accessories as per SLD.
Outgoing Side:
a) 2500 AT/AF 4P Adj. ACB Breaker = 2No.
b) 1250 AT/AF 4P Adj. ACB Breaker = 1No.
c) 1000 AT/AF 4P Adj. MCCB Breaker = 1No
d) 400 AT/AF 4P Adj. MCCB Breaker = 1No
e) with spare space for future = 2No.
f) Power Factor Correction Panel (750 kVAR with detuned Reactor = 75kVAR x 9 Steps + 25kVAR x 3 Steps) = 1No.
g) Energy (kWH) Meters comptable with BMS System = 4No
h) Including other related Accessories as per SLD.
2.7 | LSDB-P2-2 (For Tower-1&2 Life safety DB for Mech-Load rating 400V): | Nos | 1 |  | 0 |  |  | 0 |  |  | 0 |  | 4003940 | 4003940 |  | 2789140 | 2789140 | LSDB-P2-1 (Tower) | 2446313 | 2446313
(Type-Tested Panel, The cubicle roof, side panels and doors shall be of not less than 2 mm thick electro-zinc plated, 400A 4P Cooper Busbar 65kA for 1 sec /Form 4B/IP21 including Surge Protection Devices, & Energy (kWH) Meters comptable with BMS system & all related accessories necessary to complete the job in all respect as per SLD)
Incoming Side:
a) 400 AT/AF 4P Adj. MCCB Breaker MA Type = 1No.
b) Energy (kWH) Meters comptable with BMS System = 1No.
c) 400A ATS = 1No.
d) Including other related Accessories as per SLD.
Outgoing Side:
a) 160A 4P MCCB Breaker MA Type = 2No.
b) 40A 4P MCCB Breaker MA Type = 1No
c) with spare space for future = 2No.
d) Energy (kWH) Meters comptable with BMS System = 3No
e) Including other related Accessories as per SLD.
Total LV Panels (Emporium Plot-2) (Podium-2, Tower 1 & 2) Exclusive of 17% GST |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 125268090 |  |  | 123464800 |  |  | 117262290
Total LV Panels (Emporium Plot-1) (Podium-1, Tower 1 & 2) Inclusive of 17% GST |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 21295575.3 |  |  | 20989016 |  |  | 19934589.3
G.Total LV Panels (Emporium Plot-1) (Podium-1, Tower 1 & 2) Inclusive of 17% GST |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 146563665.3 |  |  | 144453816 |  |  | 137196879.3
Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Exclusive of 17% GST |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 253388820 |  |  | 247907290 |  |  | 235687317
Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Inclusive of 17% GST |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 43076099.4 |  |  | 42144239.3 |  |  | 40066843.89
G.Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Inclusive of 17% GST |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 296464919.4 |  |  | 290051529.3 |  |  | 275754160.89
A | Delivery Time
| Time to Deliver the Good at site |  |  | Delivery time is 7 ~ 8 months Ex works |  |  | 8 ~ 9 months after order confirmation & LC establishment. |  |  | 8 ~ 9 months (ex works) after Purchase Order and Clean LC with 100% payment at site. |  |  | 5 ~ 6 Months after receipt of advance payment including GST along with Purchase Order and final approval of drawings, whichever is later. |  |  | Delivery of MV/LV Switchgear will be within 4 to 6 Months from the date of advance payment and drawings approval. |  |  | Delivery 5 ~ 6 Months from the date of approval of drawings. Any delay in approval process may affect delivery schedule. All supplies are made on customer risk and account.
B | Payment Conditions
| Advance Payment |  |  | 100% advance with confirmed order / as per mutually agreed with the customer for local contents. For imported contents, complete payment to be made against irrevocable LC at sight |  |  | Confirm purchase order followed by Clean Letter of Credit at sight through a first-class bank acceptable to Green Power. |  |  | Letter of Credit of 100% of order value payable at sight. |  |  | 50% Advance Payment including GST along with Purchase Order. 50% Before delivery, upon intimation to dispatch of equipment.. |  |  | 50% advance and 50% after satisfactory inspection prior to delivery. |  |  | 70% advance for the confirmation of order and 30% before the delivery of product.
Interim Payment limit
Payment after Completion
C | Warranties & After Sale services
| Defect Liability Period |  |  | 02 year or 2000 hours whichever comes first. |  |  | 12 Months or 1,000 hours, whichever come earlier or per requirement. |  |  | The warranty period is 40-44 weeks the date of shipment from the date of Commissioning of Genset. |  |  | 12 months from the date of commissioning or 18 months from the date of shipment from IMS, whichever occurs first. |  |  | One‐year warranty against any manufacturing defects, Our liability excludes natural wear & tear, defects arising after transfer of risk, transport risks, mishandling or negligence are on part of the customer.
| Services after DLP | [5 empty] | *Subject to Operation & Maintenance as per OEM Recommendation.
| Project Manager/General Manager |  |  |  |  | Director Engineering | [5 empty] | Project Director / CEO | [6 empty] | Chairman
Note:

## Sheet1 (hidden)
Description | Siemens Energy | EARCON Group | IMS | Bilal Engineering (Pvt.) Ltd | Ravi Switchgear (Schneider Electric) | Green T&D
Total LV Panels (Emporium Plot-2) (Podium-2, Tower 1 & 2) Exclusive of 17% GST | 0 | 0 | 125268090 | 123464800 | 182655438 | 0
Total LV Panels (Emporium Plot-1) (Podium-1, Tower 1 & 2) Inclusive of 17% GST | 0 | 0 | 21295575.3 | 20989016 | 31051424.46 | 0
G.Total LV Panels (Emporium Plot-1) (Podium-1, Tower 1 & 2) Inclusive of 17% GST | 0 | 0 | 146563665.3 | 144453816 | 213706862.46 | 0
Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Exclusive of 17% GST | 0 | 0 | 253388820 | 247907290 | 366495146 | 0
Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Inclusive of 17% GST | 0 | 0 | 43076099.4 | 42144239.3 | 62304174.82 | 0
G.Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Inclusive of 17% GST | 0 | 0 | 296464919.4 | 290051529.3 | 428799320.82 | 0

## Sheet2 (hidden)
Vendor | Siemens Energy | EARCON Group | IMS Electric | Bilal Engineering | Ravi Switchgear (Schneider Electric) | Green T&D
Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Exclusive of 17% GST | 0 | 0 | 253388820 | 247907290 | 366495146 | 0
17% GST | 0 | 0 | 43076099.4 | 42144239.3 | 62304174.82 | 0
G.Total MV Panels (Emporium Plot-1 & 2) (Podium-1 & 2, Tower-1 & 2) Inclusive of 17% GST | 0 | 0 | 296464919.4 | 290051529.3 | 428799320.82 | 0