## Sheet1
SECTION-G DISTRIBUTION BOARD (DB)
G1 | Supply, installation, termination,testing & commissioning of IP 55 double door / lock, suitable for 500 volts, 3 phase, 4 wires, earth terminal AC system floor standing or wall fixed / flush / surface as required. Tinned copper bus bars to be used, inside with protection cover for cable bundles from top and bottom as standard. Complete with all components and other installation accessories as per requirements. Submit shop drawings for approval: The D.B comprises of
G1.1 | DB-B (Refer SLD) Incoming 1-450 A -15kA TP MCCB 3-500/5A Current Transformer 3-indication Lamps. 1-A meter 0-500 1-Voltmeter 0-500. 1-Ampere meter Selector Switch. 1-Voltmeter Selector Switch. 1-Control Fuse 2A SP. Outgoing 5-32 A - 15kA SP MCB 8-15 A - 6kA SP MCB 7- 10 A - 6kA SP MCB 5 - 5A - 6kA SP MCB 15 - 32A - 15kA TP MCCB 9 - 15A - 15kA TP MCCB 10 - 10A - 15kA TP MCCB | Job | 1
G1.2 | DB-M&C (Refer SLD) Incoming 1-250 A -15kA TP MCCB 3-250/5A Current Transformer 3-indication Lamps. 1-A meter 0-300 1-Voltmeter 0-500. 1-Ampere meter Selector Switch. 1-Voltmeter Selector Switch. 1-Control Fuse 2A SP. Outgoing 7- 10 A - 6kA SP MCB 3 - 5A - 6kA SP MCB 8 - 32A - 15kA TP MCCB 4 - 15A - 15kA TP MCCB 2 - 5A - 15kA TP MCCB | Job | 1
G1.3 | DB-COM (Refer SLD) Incoming 1-100 A -15kA TP MCCB 3-100/5A Current Transformer 3-indication Lamps. 1-A meter 0-100 1-Voltmeter 0-500. 1-Ampere meter Selector Switch. 1-Voltmeter Selector Switch. 1-Control Fuse 2A SP. Outgoing 2- 15 A - 6kA SP MCB 10 - 10A - 6kA SP MCB 10 - 5A - 15kA SP MCCB 6 - 15A - 15kA TP MCCB 2 - 10A - 15kA TP MCCB | Job | 1
G1.4 | DB-CIVIL (Refer SLD) Incoming 1-60 A -15kA TP MCCB 3-60/5A Current Transformer 3-indication Lamps. 1-A meter 0-100 1-Voltmeter 0-500. 1-Ampere meter Selector Switch. 1-Voltmeter Selector Switch. 1-Control Fuse 2A SP. Outgoing 5- 15 A - 6kA SP MCB 8 - 10A - 6kA SP MCB 8 - 5A - 15kA SP MCCB 3 - 15A - 15kA TP MCCB | Job | 1
G1.5 | DB-A (Refer SLD) Incoming 1-80 A -15kA TP MCCB 3-100/5A Current Transformer 3-indication Lamps. 1-A meter 0-100 1-Voltmeter 0-500. 1-Ampere meter Selector Switch. 1-Voltmeter Selector Switch. 1-Control Fuse 2A SP. Outgoing 2 - 15 A - 6kA SP MCB 3 - 5A - 15kA SP MCCB 3 - 15A - 15kA TP MCCB 5 - 10A - 15kA TP MCCB | Job | 1
G1.6 | DB-EL (Refer SLD) Incoming 1-15 A -15kA TP MCCB 3-indication Lamps. 1-A meter 0-30 1-Voltmeter 0-500. 1-Ampere meter Selector Switch. 1-Voltmeter Selector Switch. 1-Control Fuse 2A SP. Outgoing 5 - 10 A - 6kA SP MCB | Job | 1
G1.7 | DB-RTL (Refer SLD) Incoming 1-15 A -15kA TP MCCB 3-indication Lamps. 1-A meter 0-30 1-Voltmeter 0-500. 1-Ampere meter Selector Switch. 1-Voltmeter Selector Switch. 1-Control Fuse 2A SP. Outgoing 7 - 5A - 15kA SP MCCB 2 - 15A - 15kA TP MCCB | Job | 1